g

A Series® Lighting Control Panelboards

DEH41097	Rev. 2

A Series® Lighting Controller
Modbus Register Map

Introduction	1

Function Codes	1

Diagnostics	1

Objects Supported by the Lighting Controller	2

Register Types	2

Fixed-Value Registers	4

Sample Packets	4

Device Product ID	4

Latitude and Longitude	5

Last Reset	5

Device Properties (Editable)	6

Multistate Input Registers	7

Multistate Input Registers	7

Sample Packets	8

Read MI Reg1 to Reg16	8

Read MI Reg1 to Reg3	8

Read MI Reg15 to Reg18	9

Write to MI Reg15	9

Multi-State Input (MI) Enumeration	10

Analog Input Registers	12

Analog Input (AI) Value- (Registers 101-148)	12

Analog Input (AI) Object (Registers 1001 – 1272)	12

Analog Input (AI) Properties:	12

Sample packets	13

Analog Variables (AV) – Physical Input Setup	15

Physical Output Registers (Coils)	16

Sample Packets	16

Read Coil Status of BO Reg2 to Reg17	16

Read Coil Status of BO Reg2 to Reg19	17

Read Coil Status of BO Reg62 to Reg66	17

Physical Output Registers (OutOfService)	17

Sample Packets	18

Write to Output Reg201	18

Multiple Write Output Reg220–Reg229	18

Binary Output (BO) Properties:	19

Sample Packets	19

Read All BO1 Properties	19

Single Write to BO1 Override Time	20

Multiple Write to Binary Output	20

Feedback Registers	21

Sample Packets	21

Special Registers	22

Lighting Group Objects	23

Lighting Group Output Registers (Coils)	23

Sample Packets	23

Lighting Group Registers (OutOfService)	23

Sample Packets	23

Lighting Group Setup Registers	23

Sample Packets	26

Read for LG1 OutOfService Value	26

Read LG Photocell Reference	26

Read Lighting Output Array	26

Single Write OFF to Lighting Group 1	26

Read for Lighting Group 1 OutOfService	27

Single Write to Restore OutOfService	27

Read for LG1 OutOfService	27

Schedule	28

Schedule Value Registers	28

Sample Packets	28

Schedule OutOfService Registers	28

Sample Packets	28

Schedule Objects	29

Sample Packets	30

Read for Schedule OutOfService	30

Read for Schedule On and Off Times	30

Read for Schedule Day Entries	31

Multiple Write Changing a Day Schedule	32

Single Write to Remove an Entry	32

Calendar Objects	33

Calendar Object Registers	33

Sample Packets	33

Read Calendar Properties OutOfService	33

Read Calendar Properties Date List	34

Single Write of True to CAL OutOfService	34

Single Write to CAL1 Date List Count	34

Multiple Write to Edit Entry in Date List	34

Read Calendar Properties Date List	35

Multiple Write of New Entry to Date List	35

Multiple Write to Delete Entry in Date List	36

Read Calendar Properties – Date List	36

Compact Event Log	37

Event Definitions	37

Compact Event Log Registers	37

Sample Packets	39

Ask for Compact Event Log Event #1	39

Ask for Compact Event Log Total Events	39

Ask for Compact Event Log Nonexistent Event	39

Load Shedding	41

Load Shed (LS) object – (Registers 30001 – 30069)	41

Sample Packets	41

Summary of Registers	42

Table 1. Function codes supported by the Lighting Controller.	1

Table 2. Exception response codes.	1

Table 3. Object types supported by the Lighting Controller.	2

Table 4. Object ID	3

Table 5. Types of fixed-value registers.	4

Table 6. Sample packet for device product ID.	5

Table 7. Sample packet for device latitude and longitude.	5

Table 8. Sample packet for device last reset date, time, and count.	5

Table 9. Types of fixed-value registers.	6

Table 10. List of physical input registers.	7

Figure 1. Sample display of 16 switch inputs.	8

Table 11. Sample packet for read of MI Reg1 to Reg16.	8

Table 12. Sample packet for read of MI Reg1 to Reg3.	8

Table 13. Sample packet for read of MI Reg15 to Reg18.	9

Table 14. Sample packet for write of MI Reg15.	9

Table 15. Multi-state Input Configuration 1	10

Table 16. Multi-state Input Configuration 2	10

Table 17. MIC associated with each Multi-state Input	10

Table 18. Format of Multi-state Input associated MIC reference	11

Table 19. Analog Input Registers	12

Table 20. Analog Input Property Registers	12

Table 21. Property of AI1 object	13

Table 22 Sample packet for read of AI1 register	13

Table 23.Sample packet for read of AI 601 register	14

Table 24 Analog Variable Registers	15

Table 25. Analog Variable Properties	15

Table 26. List of physical output registers (coils).	16

Table 27. Sample packet for coil status of BO Reg2 to Reg17.	16

Table 28. Sample packet for coil status of BO Reg2 to Reg19.	17

Table 29. Sample packet for coil status of BO Reg62 to Reg 66.	17

Table 30. List of physical output registers (OutOfService).	18

Table 31. Sample packet for multiple write to output Reg220–Reg229.	18

Table 32. Sample packet for write to output Reg201.	18

Table 33. Binary Output (BO) Registers	19

Table 34. Address space of binary output registers.	19

Table 35. Sample packets for read of all BO1 properties.	20

Table 36. Sample packets for single write to BO1 overwrite time.	20

Table 37. Sample packets for multiple write to binary output.	20

Table 38. List of feedback registers.	21

Table 39. Sample packets for output feedback instances 1–19.	21

Table 40.Special output Registers	22

Table 41. Request to read BO67-BO70	22

Table 42. Request to write  Register 67	22

Table 43. Lighting Group output registers.	23

Table 44. Sample packets for LG Value Reg302 to Reg305.	23

Table 45. Lighting Group OutOfService registers.	23

Table 46. Sample packets for LG out of Service instance 401–416.	23

Table 47 different lighting group registers	24

Table 48. Lighting Group setup registers.	25

Table 49. Sample packets for read for Reg4001–Reg4003.	26

Table 50. Sample packets for read LG photocell reference for Reg4009–4011.	26

Table 51. Sample packets for read for lighting output array.	26

Table 52. Sample packets for single write OFF to LG 1.	26

Table 53. Sample packet for read of LG1 OutOfService.	27

Table 54. Sample packets for single write to restore OutOfService.	27

Table 55. Sample packets for read for LG1 OutOfService.	27

Table 56. Schedule value registers.	28

Table 57. Sample packets for request for SCH Value.	28

Table 58. Schedule OutOfService registers.	28

Table 59. Sample packets for request for SCH OutOfService status.	28

Table 60. Schedule Registers	29

Table 61. Schedule object registers.	30

Table 62. Sample packets for read of Schedule OutOfService.	30

Table 63. Sample packets for read of Schedule On and Off times.	30

Table 64. Sample packets for read of schedule day entries.	31

Table 65. Sample packets for multiple write changing a day schedule.	32

Table 66. Sample packets for a single write to remove an entry.	32

Table 67. Calendar (CAL) Object Registers	33

Table 68. Address space for calendar object registers.	33

Table 69. Sample packets for a read of CAL properties – OutOfService.	34

Table 70. Sample packets for a read of CAL properties – date entries.	34

Table 71. Sample packets for a single write of True to CAL1 OutOfService.	34

Table 72. Sample packets for a single write to the Date List Count Register.	34

Table 73. Sample packets for a multiple write to edit the Date List.	35

Table 74. Sample packets for a read of CAL properties – date entries.	35

Table 75. Sample packets for a multiple write of a new entry.Read Calendar Properties Date List	35

Table 76. Sample packets for a read of CAL properties – date entries.	35

Table 77. Sample packets for a multiple write to delete an entry.	36

Table 78.` Sample packets for a read of CAL properties – date entries.	36

Table 79. Registers comprising the compact event log.	37

Table 80. Event definitions	38

Table 81. Sample packets for request for compact event log event #1.	39

Table 82. Sample packets for request for compact event log total events.	39

Table 83. Sample packets for request for nonexistent event.	39

Table 84. registers to set up  alarm events and alarm output reference	40

Table 85. possible register values for every Lighting Alarm Value combination	40

Table 86. Load shed registers.	41

Table 87. Shed Level definitions	41

Table88. Simple packets for read of all LS1 properties.	41

Table 89.Summary of Registers	43

Introduction

The Lighting Controller can be configured as a Modbus Slave device using the RTU Modbus Master-Slave protocol. The Lighting Controller is always the slave and cannot initiate communications.

Function Codes

The Lighting Controller operating as a Modbus slave uses the function codes listed in Table 1.

Diagnostics

Diagnostics are supported by the Modbus protocol with the following three methods:

•	Exception Responses – When a failure occurs a diagnostic value is returned, otherwise an acknowledgement is returned.

•	Read Exception Status – Hardware-specific coil values that can be read and interpreted.

•	Function 08 –Formal layout of reporting statistics and problems.

The Lighting Controller only supports exception responses. These occur when a message is received by the Modbus slave, but the device was unable to answer due to a problem with the message, such as a request for a register that does not exist. Thorough reporting of problems is important for development, support, and use of the product. There are eight exception codes that are provided by the Modbus protocol. The remaining values in the exception byte can be assigned arbitrarily.

If the slave receives a message without a communication error, but is unable to process it, the slave returns an exception response to inform the master of the error. The high-order bit is set in the function code and returned with the characterizing exception response code, as listed in Table2.

| Function Code | Command | Purpose | Register Group |
| --- | --- | --- | --- |
| 01 | Read Coil Status | Read results or status of coils | Command coils, binary outputs |
| 02 | Read Input Status | Read physical binary inputs | Input status |
| 03 | Read Holding Registers | Reading the setpoint registers | Fixed value registers, setpoint registers |
| 04 | Read Input Registers | Reading actual value registers | Schedule event registers and feedback inputs |
| 05 | Force Single Coil | Setting the signal coil or executing single command | Command coils, binary outputs |
| 06 | Preset Single Register | Write data into register | Setpoint registers |
| 15 | Force Multiple Coils | Write data to multiple outputs | Binary outputs |
| 16 | Write Multiple Registers | Write data into multiple register | Setpoint registers, etc. |

Table 1. Function codes supported by the Lighting Controller.

| Function | Name | Purpose |
| --- | --- | --- |
| 2 | Invalid register | The Register address is not recognized or defined by the Lighting Controller. |
| 3 | Invalid data value | Data out of range |
| 83h | Partial register read | Partial property read |
| 84h | Partial register write | Partial property write |
| 85h | Write protect violation | Write to a read only property. |
| 86h | Single write entry violation | Multiple entries on single write packet, which is restricted to one entry modification due to array shuffling. NOTE: Only for LG lighting outputs and common group properties. |
| 89h | Invalid property read/write | Fail to read/write a property due to restriction. |

Table 2. Exception response codes.

Objects Supported by the Lighting Controller

The Lighting Controller supports the object types listed in

Table 3.

Register Types

All registers are defined as read only except coil and setpoint registers. Fixed-value register addresses start at 0201 and are read by function code 04. Actual-value register addresses start at 1000 and are read by function code 03. Event register addresses start at 20001 and are read by function code 04.

All registers consist of 16-bit integers, with values less than 256 stored in the lower byte. Inputs, outputs, and binary values use Modbus coils and input bit order.

The Modbus device is mapped to a BACnet database.

The Modbus object ID for BACnet object type is given in Table4.

| Object | Quantity | Comments |
| --- | --- | --- |
| DEV – Device Information | 1 per controller | Fixed registers |
| INPUTS: |  |  |
| MI – Multi-state Input | 80 = 16 inputs * 5 Modules | Switch Input Modules. |
| AI - Analog Input | 19 = 3 On-board + (8 inputs * 2 Modules) | Daylight Optimization Modules. |
| AV – Analog Variables | 16 = 8 inputs * 2 Modules | Daylight Optimization Modules. |
| OUTPUTS: |  |  |
| BO - Binary Output | 66 = Breakers 4 = Special Outputs |  |
| BV – Binary Variables | 66 | 1 Light switch per Breaker |
| Operational Control: |  |  |
| LG - Lighting Group | 16 | Each controlling up to 33 local outputs. |
| SCH – Schedule | 16 | 7 Day schedules - with 16 On/Off times per day (+ 2 Calendar references) |
| CAL – Calendar | 2 | 90 Date entries spanning 10 years |
| CEL - Compact Event Log | 1 per controller | 1500 timestamp event records |
| LS – Load Shed | 1 | 66 outputs, 5 shed levels |

Table 3. Object types supported by the Lighting Controller.

| Object Type | Object ID for MODBUS |
| --- | --- |
| AI - Analog Input | 0 |
| AO - Analog Output | 1 |
| AV - Analog Variable | 2 |
| BI - Binary Input | 3 |
| BO - Binary Output | 4 |
| BV - Binary Variable | 5 |
| CAL – Calendar | 6 |
| DEV – Device Information Object | 8 |
| CO – Control Loop | 12 |
| MI – Multi-state Input | 13 |
| MO – Multi-state Output | 14 |
| MV – Multi-state Value | 19 |
| SCH – Schedule | 17 |
| TL - Trend Log | 20 |
| AIC - Analog Input Configuration | 176 |
| BDC - Binary Device Configuration | 178 |
| MIC – Multi-state Input Configuration | 183 |
| LS – Load Shed | 182 |
| CEL – Compact Event Log | 297 |
| LNK – LINKnet Device | 299 |
| LG - Lighting Group | 303 |

Table 4. Object ID

Fixed-Value Registers

Fixed-value register addresses start at 10001 and are read by Function Code 04. They are mapped to Device properties. These properties are assigned constant values at the time of manufacture and may be stored in the onboard EEPROM rather than in the database.

The fixed-value (device object property) registers are listed in Table 5.

All strings have an embedded length. The first two registers of the string contain the length of the string; e.g., Product ID Reg10040 Hi contains the most-significant byte and Reg10040 Lo contains the least-significant byte of the string length. The first character starts at Reg10041 Hi, the second character in Reg10041 Lo, the third character in Reg10042 Hi, and so forth.

| Offset | Modbus # reg | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- |
| 0 | 10001–10007 | Firmware Version | ASCII | Int (ASCII string) 12 chars max + 2 bytes string size | R |
| 7 | 10008–10014 | Hardware Revision | ASCII | Int (ASCII string) 12 chars max + 2 bytes string size | R |
| 14 | 10015–10021 | Application software version | ASCII | Int (ASCII string) 12 chars max | R |
| 21 | 10022–10023 | Latitude1 | Real | ±90.0 | R |
| 23 | 10024–10025 | Longitude2 | Real | ±180.0 | R |
| 25 | 10026 | UTC Enable | Int | 0 /1 | R |
| 26 | 10027 | UTC Offset | Int | ±32767 | R |
| 27 | 10028 | DST Enable | Int | 0/1 | R |
| Last Reset Time/Date |
| 28 | 10029 | Hours/Minutes | Word |  | R |
| 29 | 10030 | Seconds/Hundreths sec | Word |  | R |
| 30 | 10031 | DayOfWeek/Day | Word |  | R |
| 31 | 10032 | Month/Year | Word |  | R |
| 32 | 10033 | Reset Count | Word | 1–65536 | R |
| 33 | 10034 | Device Address (Mac address) | Word | 1–99 | R |
| 34 | 10035 | Device Control | Word | See Reg 50035 | NA |
| Current Time/Date |
| 35 | 10036 | Hours/Minutes | Word |  | R |
| 36 | 10037 | Seconds/Hundredths Sec | Word |  | R |
| 37 | 10038 | DayofWeek/Day | Word |  | R |
| 38 | 10039 | Month/Year | Word |  | R |
| 39 | 10040–10046 | Product ID | ASCII | INT (ASCII string) 12 chars max + 2 bytes string size | R |

1	Latitude: positive value is north, negative value is south.

2	Longitude: positive value is east, negative value is west.

Table 5. Types of fixed-value registers.

Date and time values are represented as follows:

•	Week of day: 1–7, 255 (wildcard)

•	Day: 1–31, 255 (wildcard)

•	Month: 1–12, 255 (wildcard)

•	Year: 0–255

•	Hour: 0–23, 255 (wildcard)

•	Minutes: 0–59, 255 (wildcard)

•	Seconds: 0–59, 255 (wildcard)

•	Hundredths of seconds: 0–99, 255 (wildcard)

Sample Packets

The following are examples of packets generated by requests for specific properties.

Device Product ID

Table 6 shows the result of a request for device product ID: Reg10040 to Reg10046 (Function 04, DEV1 in map).

The response is as follows:

Reg10040 – Product Id Length – 0x000A – 10 characters

Reg10041 to Reg10046 – Product Id – 0x444C432B473136343245 – “DLC+G1642E”

All unused bytes are filled with zeros.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 27 | Byte Count | 0E |
| Register Address Lo | 37 | Reg10040 Hi | 00 |
| Quantity of Input Reg. Hi | 00 | Reg10040 Lo | 0A |
| Quantity of Input Reg. Lo | 07 | Reg10041 Hi | 44 |
| Packet CRC Hi |  | Reg10041 Lo | 4C |
| Packet CRC Lo |  | Reg10042 Hi | 43 |
|  |  | Reg10042 Lo | 2B |
|  |  | Reg10043 Hi | 47 |
|  |  | Reg10043 Lo | 31 |
|  |  | Reg10044 Hi | 36 |
|  |  | Reg10044 Lo | 34 |
|  |  | Reg10045 Hi | 32 |
|  |  | Reg10045 Lo | 45 |
|  |  | Reg10046 Hi | 00 |
|  |  | Reg10046 Lo | 00 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 6. Sample packet for device product ID.

Latitude and Longitude

Table 7 shows the result of a request for device latitude and longitude: Reg10022–Reg10025 (Function 04, DEV1 in map).

The response is as follows:

Reg10022 to Reg10023 – Latitude – 0x4226CCCD – 41.7 degrees North

Reg10024 to Reg10025 – Longitude – 0x428FCCCD – 71.9 degrees West (–71.9)

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 27 | Byte Count | 08 |
| Register Address Lo | 25 | Reg10022 Hi | 42 |
| Quantity of Input Reg. Hi | 00 | Reg10022 Lo | 26 |
| Quantity of Input Reg. Lo | 04 | Reg10023 Hi | CC |
| Packet CRC Hi |  | Reg10023 Lo | CD |
| Packet CRC Lo |  | Reg10024 Hi | C2 |
|  |  | Reg10024 Lo | 8F |
|  |  | Reg10025 Hi | CC |
|  |  | Reg10025 Lo | CD |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 7. Sample packet for device latitude and longitude.

Last Reset

Table 8 shows the result of a request for device last reset time and date and reset count: Reg10029–Reg10033 (Function 04, DEV1 in map).

The response is as follows:

Reg10029 to Reg10030 – Last Reset Time: 0x0E080400 – 14:08:04.00

Reg10031 to Reg10032 – Last Reset Date: 0x 04040368 – Thursday Mar 4, 2004

Reg10033 – Reset Count – 0x0005 – 5

- Our base year is 1900 ie. 0x68 (104)

Year = 1900+104=2004

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 27 | Byte Count | 0A |
| Register Address Lo | 2C | Reg10029 Hi | 0E |
| Quantity of Input Reg. Hi | 00 | Reg10029 Lo | 08 |
| Quantity of Input Reg. Lo | 05 | Reg10030 Hi | 04 |
| Packet CRC Hi |  | Reg10030 Lo | 00 |
| Packet CRC Lo |  | Reg10031 Hi | 04 |
|  |  | Reg10031 Lo | 04 |
|  |  | Reg10032 Hi | 03 |
|  |  | Reg10032 Lo | 68 |
|  |  | Reg10033 Hi | 00 |
|  |  | Reg10033 Lo | 05 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 8. Sample packet for device last reset date, time, and count.

Device Properties (Editable)

Table 9 indicates the editable device properties.

| Offset | Modbus # reg | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- |
| 0 | 50001 – 50007 | Firmware Version | ASCII | Int (ASCII string) 12 chars max + 2 bytes string size | R |
| 7 | 50008 – 50014 | Hardware Revision | ASCII | Int (ASCII string) 12 chars max + 2 bytes string size | R |
| 14 | 50015 – 50021 | Application software version | ASCII | Int (ASCII string) 12 chars max | R |
| 21 | 50022 – 50023 | Latitude* | Real | +/- 90.0 | R/W |
| 23 | 50024 – 50025 | Longitude** | Real | +/- 180.0 | R/W |
| 25 | 50026 | UTC Enable | INT | 0 /1 | R/W |
| 26 | 50027 | UTC Offset | INT | +/- 32767 | R/W |
| 27 | 50028 | DST Enable | INT | 0/1 | R/W |
| Last Reset Time/Date |
| 28 | 50029 | Hours/Minutes | WORD |  | R |
| 29 | 50030 | Seconds/Hundreths sec | WORD |  | R |
| 30 | 50031 | DayOfWeek/Day | WORD |  | R |
| 31 | 50032 | Month/Year | WORD |  | R |
| 32 | 50033 | Reset Count | WORD | 1 – 65535 | R |
| 33 | 50034 | Device Address (Mac address) | WORD | 1 – 99 | R |
| 34 | 50035 | Device Control | WORD | 1 - Load-from-Flash 2 - Save-to-Flash 3 - Recfg Network | W |
| Current Time/Date |
| 35 | 50036 | Hours/Minutes | WORD |  | R/W |
| 36 | 50037 | Seconds/Hundredths Sec | WORD |  | R/W |
| 37 | 50038 | DayofWeek/Day | WORD |  | R/W |
| 38 | 50039 | Month/Year | WORD |  | R/W |
| 39 | 50040 – 50046 | Product Id | ASCII | INT (ASCII string) 12 chars max + 2 bytes string size | R |

Table 9. Types of fixed-value registers.

Note:

- Registers of Type R must not be written to even though the can be viewed with Function 3.

- Registers of Type R/W are designed to be editable.  This allows setting the DST/UTC & Location.

Changing the Current time requires a single write to registers 50035 to 50038, using Function 16

Multistate Input Registers

What would normally be binary inputs for the switch inputs on the Lighting Controller are treated as multistate inputs because of the different types of switches that can be applied to these devices (LinkNet). The value is an enumerated type, which has more than two possible values. These are read only, so function 4 is used to obtain the analog values that represent the switch states.

Mapped to multistate inputs (MI) 101–116, 201–216, 301–316, 401–416, and 501–516. The Modbus address space is a contiguous block starting at 1. The value in the register represents the input’s PresentValue.

Multistate Input Registers

The multistate input registers are listed in Table10. A sample display of 16 switch inputs is shown in Figure1. Enumerated inputs can have the following values:

•	Off (Hex 01)     •	On (Hex 02) •	N/A (Hex 03)

| Reg. | Contents | Type | Format | Object Instance |  | Reg. | Contents | Type | Format | Object Instance |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | MI101 Value | R | Enumerated | 101 |  | 41 | MI309 Value | R | Enumerated | 309 |
| 2 | MI102 Value | R | Enumerated | 102 |  | 42 | MI310 Value | R | Enumerated | 310 |
| 3 | MI103 Value | R | Enumerated | 103 |  | 43 | MI311 Value | R | Enumerated | 311 |
| 4 | MI104 Value | R | Enumerated | 104 |  | 44 | MI312 Value | R | Enumerated | 312 |
| 5 | MI105 Value | R | Enumerated | 105 |  | 45 | MI313 Value | R | Enumerated | 313 |
| 6 | MI106 Value | R | Enumerated | 106 |  | 46 | MI314 Value | R | Enumerated | 314 |
| 7 | MI107 Value | R | Enumerated | 107 |  | 47 | MI315 Value | R | Enumerated | 315 |
| 8 | MI108 Value | R | Enumerated | 108 |  | 48 | MI316 Value | R | Enumerated | 316 |
| 9 | MI109 Value | R | Enumerated | 109 |  | 49 | MI401 Value | R | Enumerated | 401 |
| 10 | MI110 Value | R | Enumerated | 110 |  | 50 | MI402 Value | R | Enumerated | 402 |
| 11 | MI111 Value | R | Enumerated | 111 |  | 51 | MI403 Value | R | Enumerated | 403 |
| 12 | MI112 Value | R | Enumerated | 112 |  | 52 | MI404 Value | R | Enumerated | 404 |
| 13 | MI113 Value | R | Enumerated | 113 |  | 53 | MI405 Value | R | Enumerated | 405 |
| 14 | MI114 Value | R | Enumerated | 114 |  | 54 | MI406 Value | R | Enumerated | 406 |
| 15 | MI115 Value | R | Enumerated | 115 |  | 55 | MI407 Value | R | Enumerated | 407 |
| 16 | MI116 Value | R | Enumerated | 116 |  | 56 | MI408 Value | R | Enumerated | 408 |
| 17 | MI201 Value | R | Enumerated | 201 |  | 57 | MI409 Value | R | Enumerated | 409 |
| 18 | MI202 Value | R | Enumerated | 202 |  | 58 | MI410 Value | R | Enumerated | 410 |
| 19 | MI203 Value | R | Enumerated | 203 |  | 59 | MI411 Value | R | Enumerated | 411 |
| 20 | MI204 Value | R | Enumerated | 204 |  | 60 | MI412 Value | R | Enumerated | 412 |
| 21 | MI205 Value | R | Enumerated | 205 |  | 61 | MI413 Value | R | Enumerated | 413 |
| 22 | MI206 Value | R | Enumerated | 206 |  | 62 | MI414 Value | R | Enumerated | 414 |
| 23 | MI207 Value | R | Enumerated | 207 |  | 63 | MI415 Value | R | Enumerated | 415 |
| 24 | MI208 Value | R | Enumerated | 208 |  | 64 | MI416 Value | R | Enumerated | 416 |
| 25 | MI209 Value | R | Enumerated | 209 |  | 65 | MI501 Value | R | Enumerated | 501 |
| 26 | MI210 Value | R | Enumerated | 210 |  | 66 | MI502 Value | R | Enumerated | 502 |
| 27 | MI211 Value | R | Enumerated | 211 |  | 67 | Reserved | - | - | 503 |
| 28 | MI212 Value | R | Enumerated | 212 |  | 68 | Reserved | - | - | 504 |
| 29 | MI213 Value | R | Enumerated | 213 |  | 69 | Reserved | - |  | 505 |
| 30 | MI214 Value | R | Enumerated | 214 |  | 70 | Reserved | - | - | 506 |
| 31 | MI215 Value | R | Enumerated | 215 |  | 71 | Reserved | - | - | 507 |
| 32 | MI216 Value | R | Enumerated | 216 |  | 72 | Reserved | - | - | 508 |
| 33 | MI301 Value | R | Enumerated | 301 |  | 73 | Reserved | - | - | 509 |
| 34 | MI302 Value | R | Enumerated | 302 |  | 74 | Reserved | - | - | 510 |
| 35 | MI303 Value | R | Enumerated | 303 |  | 75 | Reserved | - | - | 511 |
| 36 | MI304 Value | R | Enumerated | 304 |  | 76 | Reserved | - | - | 512 |
| 37 | MI305 Value | R | Enumerated | 305 |  | 77 | Reserved | - | - | 513 |
| 38 | MI306 Value | R | Enumerated | 306 |  | 78 | Reserved | - | - | 514 |
| 39 | MI307 Value | R | Enumerated | 307 |  | 79 | Reserved | - | - | 515 |
| 40 | MI308 Value | R | Enumerated | 308 |  | 80 | Reserved | - | - | 516 |

Table 10. List of physical input registers.

Figure 1. Sample display of 16 switch inputs.

Sample Packets

The following are examples of packets generated by requests for specific groups of inputs.

Read MI Reg1 to Reg16

Table 11 shows the result of a request to read MI Reg1 to Reg16 (Function 4, MI 101–116 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 00 | Byte Count | 20 |
| Register Address Lo | 00 | Input 101 Hi | 00 |
| Quantity of Input Reg. Hi | 00 | Input 101 Lo | 01 |
| Quantity of Input Reg. Lo | 10 | Input 102 Hi | 00 |
| Packet CRC Hi |  | Input 102 Lo | 02 |
| Packet CRC Lo |  | Input 103 Hi | 00 |
|  |  | Input 103 Lo | 02 |
|  |  | Input 104 Hi | 00 |
|  |  | Input 104 Lo | 02 |
|  |  | Input 105 Hi | 00 |
|  |  | Input 105 Lo | 01 |
|  |  | Input 106 Hi | 00 |
|  |  | Input 106 Lo | 01 |
|  |  | Input 107 Hi | 00 |
|  |  | Input 107 Lo | 01 |
|  |  | Input 108 Hi | 00 |
|  |  | Input 108 Lo | 01 |
|  |  | Input 109 Hi | 00 |
|  |  | Input 109 Lo | 01 |
|  |  | Input 110 Hi | 00 |
|  |  | Input 110 Lo | 01 |
|  |  | Input 111 Hi | 00 |
|  |  | Input 111 Lo | 03 |
|  |  | Input 112 Hi | 00 |
|  |  | Input 112 Lo | 03 |
|  |  | Input 113 Hi | 00 |
|  |  | Input 113 Lo | 03 |
|  |  | Input 114 Hi | 00 |
|  |  | Input 114 Lo | 03 |
|  |  | Input 115 Hi | 00 |
|  |  | Input 115 Lo | 03 |
|  |  | Input 116 Hi | 00 |
|  |  | Input 116 Lo | 03 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 11. Sample packet for read of MI Reg1 to Reg16.

Read MI Reg1 to Reg3

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 00 | Byte Count | 06 |
| Register Address Lo | 00 | Input 101 Hi | 00 |
| Quantity of Input Reg. Hi | 00 | Input 101 Lo | 01 |
| Quantity of Input Reg. Lo | 03 | Input 102 Hi | 00 |
| Packet CRC Hi |  | Input 102 Lo | 02 |
| Packet CRC Lo |  | Input 103 Hi | 00 |
|  |  | Input 103 Lo | 02 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 12. Sample packet for read of MI Reg1 to Reg3.

Table 12 shows the result of a request to read MI Reg1 to Reg3 (Function 4, MI 101–103 in map).

Read MI Reg15 to Reg18

Table 13 shows the result of a request to read MI Reg15 to Reg18 (Function 4, MI115–MI116 and MI201–MI202 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 00 | Byte Count | 08 |
| Register Address Lo | 0E | Input 115 Hi | 00 |
| Quantity of Input Reg. Hi | 00 | Input 115 Lo | 01 |
| Quantity of Input Reg. Lo | 04 | Input 116 Hi | 00 |
| Packet CRC Hi |  | Input 116 Lo | 02 |
| Packet CRC Lo |  | Input 201 Hi | 00 |
|  |  | Input 201 Lo | 01 |
|  |  | Input 202 Hi | 00 |
|  |  | Input 202 Lo | 03 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 13. Sample packet for read of MI Reg15 to Reg18.

Write to MI Reg15

Table 14 shows the result of a write to MI Reg15 (Function 5 Single Write, MI115 in map). Note that the packet shows an error, since MI values are read only.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 05 | Error Code | 85 |
| Register Address Hi | 00 | Exception Code | 85 |
| Register Address Lo | 0E | Packet CRC Hi |  |
| Quantity of Input Reg. Hi | 00 | Packet CRC Lo |  |
| Quantity of Input Reg. Lo | 01 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 14. Sample packet for write of MI Reg15.

Multi-State Input (MI) Enumeration

Each Multi-state Input has an associated Multi-state Input Configuration (MIC) object  that defines how the raw analog input value is  translated in  an enumerated value. The controller database defines two of these MIC  tables (Table 15 & 16)

|  | State # | State Name | Voltage Range |
| --- | --- | --- | --- |
| MIC1 | 1 | Off | 4-5 |
|  | 2 | On | 0-2 |
|  | 3 | N/A | 2-4 |

Table 15. Multi-state Input Configuration 1

|  | State # | State Name | Voltage Range |
| --- | --- | --- | --- |
| MIC2 | 1 | Off | 4-5 |
|  | 2 | On | 0-2 |

Table 16. Multi-state Input Configuration 2

The MIC associated with each Multi-state Input is contained in the registers detailed in table 17.

| Register | MI Input | Type | Default |
| --- | --- | --- | --- |
| 40001-40003 | MI-101 MIC | RW | MIC1 |
| 40004-40006 | MI-102 MIC | RW | MIC1 |
| 40007-40009 | MI-103 MIC | RW | MIC1 |
| 40010-40012 | MI-104 MIC | RW | MIC1 |
| 40013-40015 | MI-105 MIC | RW | MIC1 |
| 40016-40018 | MI-106 MIC | RW | MIC1 |
| 40019-40021 | MI-107 MIC | RW | MIC1 |
| 40022-40024 | MI-108 MIC | RW | MIC1 |
| 40025-40027 | MI-109 MIC | RW | MIC1 |
| 40028-40030 | MI-110 MIC | RW | MIC1 |
| 40031-40033 | MI-111 MIC | RW | MIC1 |
| 40034-40036 | MI-112 MIC | RW | MIC1 |
| 40037-40039 | MI-113 MIC | RW | MIC1 |
| 40040-40042 | MI-114 MIC | RW | MIC1 |
| 40043-40045 | MI-115 MIC | RW | MIC1 |
| 40046-40048 | MI-116 MIC | RW | MIC1 |
| 40101-40103 | MI-201 MIC | RW | MIC1 |
| 40204-40106 | MI-202 MIC | RW | MIC1 |
| 40107-40109 | MI-203 MIC | RW | MIC1 |
| 40110-40112 | MI-204 MIC | RW | MIC1 |
| 40113-40115 | MI-205 MIC | RW | MIC1 |
| 40116-40118 | MI-206 MIC | RW | MIC1 |
| 40119-40121 | MI-207 MIC | RW | MIC1 |
| 40122-40124 | MI-208 MIC | RW | MIC1 |
| 40125-40127 | MI-209 MIC | RW | MIC1 |
| 40128-40130 | MI-210 MIC | RW | MIC1 |
| 40131-40133 | MI-211 MIC | RW | MIC1 |
| 40134-40136 | MI-212 MIC | RW | MIC1 |
| 40137-40139 | MI-213 MIC | RW | MIC1 |
| 40140-40142 | MI-214 MIC | RW | MIC1 |
| 40143-40145 | MI-215 MIC | RW | MIC1 |
| 40146-40148 | MI-216 MIC | RW | MIC1 |
| 40201-40203 | MI-301 MIC | RW | MIC1 |
| 40204-40206 | MI-302 MIC | RW | MIC1 |
| 40207-40209 | MI-303 MIC | RW | MIC1 |
| 40210-40212 | MI-304 MIC | RW | MIC1 |
| 40213-40215 | MI-305 MIC | RW | MIC1 |
| 40216-40218 | MI-306 MIC | RW | MIC1 |
| 40219-40221 | MI-307 MIC | RW | MIC1 |
| 40222-40224 | MI-308 MIC | RW | MIC1 |
| 40225-40227 | MI-309 MIC | RW | MIC1 |
| 40228-40230 | MI-310 MIC | RW | MIC1 |
| 40231-40233 | MI-311 MIC | RW | MIC1 |
| 40234-40236 | MI-312 MIC | RW | MIC1 |
| 40237-40239 | MI-313 MIC | RW | MIC1 |
| 40240-40242 | MI-314 MIC | RW | MIC1 |
| 40243-40245 | MI-315 MIC | RW | MIC1 |
| 40246-40248 | MI-316 MIC | RW | MIC1 |
| 40301-40303 | MI-401 MIC | RW | MIC1 |
| 40304-40306 | MI-402 MIC | RW | MIC1 |
| 40307-40309 | MI-403 MIC | RW | MIC1 |
| 40310-40312 | MI-404 MIC | RW | MIC1 |
| 40313-40315 | MI-405 MIC | RW | MIC1 |
| 40316-40318 | MI-406 MIC | RW | MIC1 |
| 40319-40321 | MI-407 MIC | RW | MIC1 |
| 40322-40324 | MI-408 MIC | RW | MIC1 |
| 40325-40327 | MI-409 MIC | RW | MIC1 |
| 40328-40330 | MI-410 MIC | RW | MIC1 |
| 40331-40333 | MI-411 MIC | RW | MIC1 |
| 40334-40336 | MI-412 MIC | RW | MIC1 |
| 40337-40339 | MI-413 MIC | RW | MIC1 |
| 40340-40342 | MI-414 MIC | RW | MIC1 |
| 40343-40345 | MI-415 MIC | RW | MIC1 |
| 40346-40348 | MI-416 MIC | RW | MIC1 |
| 40401-40403 | MI-501 MIC | RW | MIC1 |
| 40404-40406 | MI-502 MIC | RW | MIC1 |
| 40407-40409 | Reserved | - | - |
| 40410-40412 | Reserved | - | - |
| 40413-40415 | Reserved | - | - |
| 40416-40418 | Reserved | - | - |
| 40419-40421 | Reserved | - | - |
| 40422-40424 | Reserved | - | - |
| 40425-40427 | Reserved | - | - |
| 40428-40430 | Reserved | - | - |
| 40431-40433 | Reserved | - | - |
| 40434-40436 | Reserved | - | - |
| 40437-40439 | Reserved | - | - |
| 40440-40442 | Reserved | - | - |
| 40443-40445 | Reserved | - | - |
| 40446-40448 | Reserved | - | - |

Table 17. MIC associated with each Multi-state Input

The format of the Multi-state Input’s associated MIC reference is shown in table 18.  Changing the MIC reference changes how the Multi-state Input’s value is interpreted. (Ex for MI-301).

| Offset | Modbus Reg | DB Size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 40201 | WORD | Value From | Int | 0 – 2 0 = MIC Standard 1 = reserved 2 = MIC Stepping | RW |
|  |  |  | Configuration Ref. |  |  |  |
| 1 | 40202 | WORD | Object Type | Word | 183 [MIC] | RW |
| 2 | 40203 | WORD | Object Instance | Word | 1 = MIC1 (GE Switch) 2 = MIC2 (On/Off) | RW |
|  |  |  | 3 registers per MI |  |  |  |

Table 18. Format of Multi-state Input associated MIC reference

Note: Configuration Reference registers (i.e. 40202 and 40203) must be written in a single write using Function 16.

Analog Input Registers

Lighting controller contains three on-board Analog Inputs and upto 16 remote Inputs ( 8 per Daylight Optimisation module . The present value of the Analog Input objects are mapped as indicated in table 19.

Analog Input (AI) Value- (Registers 101-148)

| Register | AI Input | Type | Format |
| --- | --- | --- | --- |
| 101 – 102 | AI1 On-board | R | Float |
| 103 – 104 | AI2 On-board | R | Float |
| 105 – 106 | AI3 On-board | R | Float |
| 117 – 118 | AI-601 | R | Float |
| 119 – 120 | AI-602 | R | Float |
| 121 – 122 | AI-603 | R | Float |
| 123 – 124 | AI-604 | R | Float |
| 125 – 126 | AI-605 | R | Float |
| 127 – 128 | AI-606 | R | Float |
| 129 – 130 | AI-607 | R | Float |
| 131 – 132 | AI-608 | R | Float |
| 133 – 134 | AI-701 | R | Float |
| 135 – 136 | AI-702 | R | Float |
| 137 – 138 | AI-703 | R | Float |
| 139 – 140 | AI-704 | R | Float |
| 141 – 142 | AI-705 | R | Float |
| 143 – 144 | AI-706 | R | Float |
| 145 – 146 | AI-707 | R | Float |
| 147 – 148 | AI-708 | R | Float |

Table 19. Analog Input Registers

Analog Input (AI) Object (Registers 1001 – 1272)

Table 20 shows different registers associated with each AI.

| Register | AI Input | Type | Conf Ref |
| --- | --- | --- | --- |
| 1001 – 1009 | AI1 On-board | RW |  |
| 1010 – 1018 | AI2 On-board | RW |  |
| 1019 – 1027 | AI3 On-board | RW |  |
| 1101 – 1109 | AI-601 | RW | AIC1 |
| 1110 – 1118 | AI-602 | RW | AIC1 |
| 1119 – 1127 | AI-603 | RW | AIC1 |
| 1128 – 1136 | AI-604 | RW | AIC1 |
| 1137 – 1145 | AI-605 | RW | AIC1 |
| 1146 – 1154 | AI-606 | RW | AIC1 |
| 1155 – 1163 | AI-607 | RW | AIC1 |
| 1164 – 1172 | AI-608 | RW | AIC1 |
| 1201 – 1209 | AI-701 | RW | AIC1 |
| 1210 – 1218 | AI-702 | RW | AIC1 |
| 1219 – 1227 | AI-703 | RW | AIC1 |
| 1228 – 1236 | AI-704 | RW | AIC1 |
| 1237 – 1245 | AI-705 | RW | AIC1 |
| 1246 – 1254 | AI-706 | RW | AIC1 |
| 1255 – 1263 | AI-707 | RW | AIC1 |
| 1264 – 1272 | AI-708 | RW | AIC1 |

Table 20. Analog Input Property Registers

Analog Input (AI) Properties:

Each AI object exposes the following properties via Function codes 3/6/16.  There are 6 properties available: Value, Calibration and Configuration Ref properties take multiple registers and Value & Reliability can only be written if OutOfService is True.  To remove a Configuration Ref, write 0 into the corresponding registers for object type and instance.

Table 21 shows different registers of AI1 object.

| Offset | Modbus Regs | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 1001 | Bit | OutOfService | Int | 0 – 1 | RW |
| 1 | 1002 | FLOAT Hi | Value * |  | 0 – 65535 | RW |
| 2 | 1003 | FLOAT Lo |  |  | 0 – 65535 | RW |
| 3 | 1004 | FLOAT Hi | Calibration |  | 0 – 65535 | RW |
| 4 | 1005 | FLOAT Lo |  |  | 0 – 65535 | RW |
| 5 | 1006 | Bit | Commissioned | Int | 0 – 1 | RW |
| 6 | 1007 | WORD | Reliability | Int | Enum | R |
|  |  |  | Configuration Ref. |  |  |  |
| 7 | 1008 | WORD | Object Type |  | 176 [AIC] | RW |
| 8 | 1009 | WORD | Object Instance |  | 1 – 65535 1 = Photodiode Linear 2 = Photoconductive 3 = Photodiode Linear (Inverse) 4 = Photoconductive (Inverse) | RW |
|  |  |  | 9 registers per AI |  |  |  |

Table 21. Property of AI1 object

Note:

- AIC reference registers 1008 and 1009 must be written in a single write using Function 16.

- Analog Input Configuration (AIC) object type in Hexadecimal is <00B0>

Sample packets

Table 22  indicates the result of read request for AI1 object

| Request | Response |
| --- | --- |
| Field Name | (Hex) | Field Name | (Hex) |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Starting Address Hi | 03 | Byte Count | 0E |
| Starting Address Lo | E8 | Reg. Value Hi (1001) | 00 |
| Quantity of Input Reg. Hi | 00 | Reg. Value Lo (1001) | 00 |
| Quantity of Input Reg. Lo | 07 | Reg. Value Hi (1002) | 41 |
| Packet CRC Hi |  | Reg. Value Lo (1002) | A0 |
| Packet CRC Lo |  | Reg. Value Hi (1003) | 00 |
|  |  | Reg. Value Lo (1003) | 00 |
|  |  | Reg. Value Hi (1004) | 40 |
|  |  | Reg. Value Lo (1004) | A0 |
|  |  | Reg. Value Hi (1005) | 00 |
|  |  | Reg. Value Lo (1005) | 00 |
|  |  | Reg. Value Hi (1006) | 00 |
|  |  | Reg. Value Lo (1006) | 01 |
|  |  | Reg. Value Hi (1007) | 00 |
|  |  | Reg. Value Lo (1007) | 00 |
|  |  | Reg. Value Hi (1008) | 00 |
|  |  | Reg. Value Low(1008) | 0B |
|  |  | Reg. Value Hi (1009) | 00 |
|  |  | Reg. Value Low(1009) | 01 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 22 Sample packet for read of AI1 register

NOTE: Response for AI1 properties

- Reg1001 (OutOfService) 0x0000 – FALSE,

- Reg1002 – 1003 (Value) 0x41A00000 – 20.0

- Reg1004 – 1005 (Calibration) 0x40A00000 – 5.0,

- Reg1006 (Commission) 0x0001 – TRUE,

- Reg1007 (Reliability) 0x0000 – Normal,

- Reg1008 – 1009 (Configuration Reference) 0x000B0001 – AIC1

Table 23 shows the result of read request for AI601 object (Registers 1101-1109)

Read entire AI601 object – Registers 1101-1109

| Request | Response |
| --- | --- |
| Field Name | (Hex) | Field Name | (Hex) |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Starting Address Hi | 04 | Byte Count | 0E |
| Starting Address Lo | 4C | Reg. Value Hi (1101) | 00 |
| Quantity of Input Reg. Hi | 00 | Reg. Value Lo (1101) | 00 |
| Quantity of Input Reg. Lo | 07 | Reg. Value Hi (1102) | 42 |
| Packet CRC Hi |  | Reg. Value Lo (1102) | C8 |
| Packet CRC Lo |  | Reg. Value Hi (1103) | 00 |
|  |  | Reg. Value Lo (1103) | 00 |
|  |  | Reg. Value Hi (1104) | 3F |
|  |  | Reg. Value Lo (1104) | 80 |
|  |  | Reg. Value Hi (1105) | 00 |
|  |  | Reg. Value Lo (1105) | 00 |
|  |  | Reg. Value Hi (1106) | 00 |
|  |  | Reg. Value Lo (1106) | 01 |
|  |  | Reg. Value Hi (1107) | 00 |
|  |  | Reg. Value Lo (1107) | 00 |
|  |  | Reg. Value Hi (1108) | 00 |
|  |  | Reg. Value Lo (1108) | 0B |
|  |  | Reg. Value Hi (1109) | 00 |
|  |  | Reg. Value Lo (1109) | 01 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 23.Sample packet for read of AI 601 register

NOTE: Response for AI601 properties

- Reg1001 (OutOfService) 0x0000 – FALSE

- Reg1002 – 1003 (Value) 0x42C80000 – 100.0

- Reg1004 – 1005 (Calibration) 0x3F800000 – 1.0

- Reg1006 (Commission) 0x0001 – TRUE

- Reg1007 (Reliability) 0x0000 – Normal

- Reg1008 – 1009 (Configuration Reference) 0x00B00001 – AIC1

Analog Variables (AV) – Physical Input Setup

The input value behavior of the two remote (Daylight Optimization) boards can be altered by adjusting the parameters represented by the Analog Variables AV601-AV632 & AV701-AV732.

## Analog Variable (AV) Object – (Registers 1301-1364 & 1401-1464)

The Analog Input Parameters (i.e. AV Present Value) are mapped as follows (Table 24):

| Input | Set Point (SP) Registers | Proportional Band Registers | Reset Rate (RR) Registers | Output Value (OP)* Register |
| --- | --- | --- | --- | --- |
| AI-601 | 1301 – 1302 (AV601) | 1317 – 1318 (AV609) | 1333 – 1334 (AV617) | 1349 – 1350 (AV625) |
| AI-602 | 1303 – 1304 (AV602) | 1319 – 1320 (AV610) | 1335 – 1336 (AV618) | 1351 – 1352 (AV626) |
| AI-603 | 1305 – 1306 (AV603) | 1321 – 1322 (AV611) | 1337 – 1338 (AV619) | 1353 – 1354 (AV627) |
| AI-604 | 1307 – 1308 (AV604) | 1323 – 1324 (AV612) | 1339 – 1340 (AV620) | 1355 – 1356 (AV628) |
| AI-605 | 1309 – 1310 (AV605) | 1325 – 1326 (AV613) | 1341 – 1342 (AV621) | 1357 – 1358 (AV629) |
| AI-606 | 1311 – 1312 (AV606) | 1327 – 1328 (AV614) | 1343 – 1344 (AV622) | 1359 – 1360 (AV630) |
| AI-607 | 1313 – 1314 (AV607) | 1329 – 1330 (AV615) | 1345 – 1346 (AV623) | 1361 – 1362 (AV631) |
| AI-608 | 1315 – 1316 (AV608) | 1331 – 1332 (AV616) | 1347 – 1348 (AV624) | 1363 – 1364 (AV632) |
| AI-701 | 1401 – 1402 (AV701) | 1417 – 1418 (AV709) | 1433 – 1434 (AV717) | 1449 – 1450 (AV725) |
| AI-702 | 1403 – 1404 (AV702) | 1419 – 1420 (AV710) | 1435 – 1436 (AV718) | 1451 – 1452 (AV726) |
| AI-703 | 1405 – 1406 (AV703) | 1421 – 1422 (AV711) | 1437 – 1438 (AV719) | 1453 – 1454 (AV727) |
| AI-704 | 1407 – 1408 (AV704) | 1423 – 1424 (AV712) | 1439 – 1440 (AV720) | 1455 – 1456 (AV728) |
| AI-705 | 1409 – 1410 (AV705) | 1425 – 1426 (AV713) | 1441 – 1442 (AV721) | 1457 – 1458 (AV729) |
| AI-706 | 1411 – 1412 (AV706) | 1427 – 1428 (AV714) | 1443 – 1444 (AV722) | 1459 – 1460 (AV730) |
| AI-707 | 1413 – 1414 (AV707) | 1429 – 1430 (AV715) | 1445 – 1446 (AV723) | 1461 – 1462 (AV731) |
| AI-708 | 1415 – 1416 (AV708) | 1431 – 1432 (AV716) | 1447 – 1448 (AV724) | 1463 – 1464 (AV732) |

Table 24 Analog Variable Registers

*Setting SP= -1 allows writing of the Output Value.

**Note: do NOT write to any of these registers without specific knowledge of the consequence

## Analog Variable (AV) Properties

Each AV object exposes the following properties (Table25) via Function codes 3/6/16.

| Offset | Modbus Regs | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 1301 – 1302 | FLOAT Hi | Value |  | 0 – 65535 | RW |
|  |  |  | 2 registers per AV |  |  |  |

Table 25. Analog Variable Properties

Physical Output Registers (Coils)

Lighting controller supports up to 66 breaker outputs (BO). Actual value registers start at 1, commanded by Function Codes 01, 05, and 15 and are mapped to Binary Outputs (BO) 1–66. The value in the register represents the Binary Output’s present value when read. Writes go to priority level 5. Writes will only be accepted if the ‘OutOfService’ flag is set for that particular output.

A value of 1 represents ON and a value of 0 represents OFF.

The physical output registers (coils) are listed in Table 26.

| Reg. | Contents | Type | Format | BO Instance |
| --- | --- | --- | --- | --- |
| 1 | BO1 Value | RW | Bit | 01 |
| 2 | BO2 Value | RW | Bit | 02 |
| 3 | BO3 Value | RW | Bit | 03 |
| 4 | BO4 Value | RW | Bit | 04 |
| 5 | BO5 Value | RW | Bit | 05 |
| 6 | BO6 Value | RW | Bit | 06 |
| 7 | BO7 Value | RW | Bit | 07 |
| 8 | BO8 Value | RW | Bit | 08 |
| 9 | BO9 Value | RW | Bit | 09 |
| 10 | BO10 Value | RW | Bit | 10 |
| 11 | BO11 Value | RW | Bit | 11 |
| 12 | BO12 Value | RW | Bit | 12 |
| 13 | BO13 Value | RW | Bit | 13 |
| 14 | BO14 Value | RW | Bit | 14 |
| 15 | BO15 Value | RW | Bit | 15 |
| 16 | BO16 Value | RW | Bit | 16 |
| 17 | BO17 Value | RW | Bit | 17 |
| 18 | BO18 Value | RW | Bit | 18 |
| 19 | BO19 Value | RW | Bit | 19 |
| 20 | BO20 Value | RW | Bit | 20 |
| 21 | BO21 Value | RW | Bit | 21 |
| 22 | BO22 Value | RW | Bit | 22 |
| 23 | BO23 Value | RW | Bit | 23 |
| 24 | BO24 Value | RW | Bit | 24 |
| 25 | BO25 Value | RW | Bit | 25 |
| 26 | BO26 Value | RW | Bit | 26 |
| 27 | BO27 Value | RW | Bit | 27 |
| 28 | BO28 Value | RW | Bit | 28 |
| 29 | BO29 Value | RW | Bit | 29 |
| 30 | BO30 Value | RW | Bit | 30 |
| 31 | BO31 Value | RW | Bit | 31 |
| 32 | BO32 Value | RW | Bit | 32 |
| 33 | BO33 Value | RW | Bit | 33 |
| 34 | BO34 Value | RW | Bit | 34 |
| 35 | BO35 Value | RW | Bit | 35 |
| 36 | BO36 Value | RW | Bit | 36 |
| 37 | BO37 Value | RW | Bit | 37 |
| 38 | BO38 Value | RW | Bit | 38 |
| 39 | BO39 Value | RW | Bit | 39 |
| 40 | BO40 Value | RW | Bit | 40 |
| 41 | BO41 Value | RW | Bit | 41 |
| 42 | BO42 Value | RW | Bit | 42 |
| 43 | BO43 Value | RW | Bit | 43 |
| 44 | BO44 Value | RW | Bit | 44 |
| 45 | BO45 Value | RW | Bit | 45 |
| 46 | BO46 Value | RW | Bit | 46 |
| 47 | BO47 Value | RW | Bit | 47 |
| 48 | BO48 Value | RW | Bit | 48 |
| 49 | BO49 Value | RW | Bit | 49 |
| 50 | BO50 Value | RW | Bit | 50 |
| 51 | BO51 Value | RW | Bit | 51 |
| 52 | BO52 Value | RW | Bit | 52 |
| 53 | BO53 Value | RW | Bit | 53 |
| 54 | BO54 Value | RW | Bit | 54 |
| 55 | BO55 Value | RW | Bit | 55 |
| 56 | BO56 Value | RW | Bit | 56 |
| 57 | BO57 Value | RW | Bit | 57 |
| 58 | BO58 Value | RW | Bit | 58 |
| 59 | BO59 Value | RW | Bit | 59 |
| 60 | BO60 Value | RW | Bit | 60 |
| 61 | BO61 Value | RW | Bit | 61 |
| 62 | BO62 Value | RW | Bit | 62 |
| 63 | BO63 Value | RW | Bit | 63 |
| 64 | BO64 Value | RW | Bit | 64 |
| 65 | BO65 Value | RW | Bit | 65 |
| 66 | BO66 Value | RW | Bit | 66 |

Table 26. List of physical output registers (coils).

Sample Packets

The following are examples of packets generated by requests for specific groups of outputs.

Read Coil Status of BO Reg2 to Reg17

Table 27 shows the result of a request to read the coil status of BO Reg2–Reg17 (Function 1, BO2–17 in map). Note that the status of outputs 9–2 is shown as the byte value 0xAC or binary 1010 1100 and output 2 is the LSB.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 00 | Byte Count | 02 |
| Register Address Lo | 01 | Output Status 9–2 | AC |
| Quantity of Outputs Hi | 00 | Output Status 17–10 | 0A |
| Quantity of Outputs Lo | 10 | Packet CRC Hi |  |
| Packet CRC Hi |  | Packet CRC Lo |  |
| Packet CRC Lo |  |  |  |

Table 27. Sample packet for coil status of BO Reg2 to Reg17.

Read Coil Status of BO Reg2 to Reg19

Table 28 shows the result of a request to read the coil status of BO Reg2–Reg19 (Function 1, BO2–19 in map). Note that the status of outputs 19–18 is shown as the byte value 0x03 or binary 0000 0011 and output 18 is the LSB. The six remaining high-order bits are zero filled.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 00 | Byte Count | 03 |
| Register Address Lo | 01 | Output Status 9–2 | AC |
| Quantity of Outputs Hi | 00 | Output Status 17–10 | 0A |
| Quantity of Outputs Lo | 12 | Output Status 19–18 | 03 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 28. Sample packet for coil status of BO Reg2 to Reg19.

Read Coil Status of BO Reg62 to Reg66

Table 29 shows the result of a request to read the coil status of BO Reg62–Reg66 (Function 1, BO62–66). Note that the status of outputs 66–62 is shown as the byte value 0x37 or binary 0001 0111 and output 62 is the LSB. The remaining two high-order bits are zero filled.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 00 | Byte Count | 03 |
| Register Address Lo | 3D | Output Status 66–62 | 17 |
| Quantity of Outputs Hi | 00 | Packet CRC Hi |  |
| Quantity of Outputs Lo | 05 | Packet CRC Lo |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 29. Sample packet for coil status of BO Reg62 to Reg 66.

The output values are

Reg62: BO62 Value – ON

Reg63: BO63 Value – ON

Reg64: BO64 Value – ON

Reg65: BO65 Value – OFF

Reg66: BO66 Value – ON

Physical Output Registers (OutOfService)

Actual value registers start at 201, commanded by Function Code 01, 05, or 15 and mapped to Binary Outputs (BO) 1–66. The address space is reserved to 900. The value in the register represents the Binary Output’s OutOfService value. A value of 1 corresponds to manual mode, 0 to auto mode.The physical output registers (OutOfService) are listed in Table 30.

| Reg. | Contents | Type | Format | BO Instance |
| --- | --- | --- | --- | --- |
| 201 | BO1 OutOfService | RW | ON/OFF | 01 |
| 202 | BO2 OutOfService | RW | ON/OFF | 02 |
| 203 | BO3 OutOfService | RW | ON/OFF | 03 |
| 204 | BO4 OutOfService | RW | ON/OFF | 04 |
| 205 | BO5 OutOfService | RW | ON/OFF | 05 |
| 206 | BO6 OutOfService | RW | ON/OFF | 06 |
| 207 | BO7 OutOfService | RW | ON/OFF | 07 |
| 208 | BO8 OutOfService | RW | ON/OFF | 08 |
| 209 | BO9 OutOfService | RW | ON/OFF | 09 |
| 210 | BO10 OutOfService | RW | ON/OFF | 10 |
| 211 | BO11 OutOfService | RW | ON/OFF | 11 |
| 212 | BO12 OutOfService | RW | ON/OFF | 12 |
| 213 | BO13 OutOfService | RW | ON/OFF | 13 |
| 214 | BO14 OutOfService | RW | ON/OFF | 14 |
| 215 | BO15 OutOfService | RW | ON/OFF | 15 |
| 216 | BO16 OutOfService | RW | ON/OFF | 16 |
| 217 | BO17 OutOfService | RW | ON/OFF | 17 |
| 218 | BO18 OutOfService | RW | ON/OFF | 18 |
| 219 | BO19 OutOfService | RW | ON/OFF | 19 |
| 220 | BO20 OutOfService | RW | ON/OFF | 20 |
| 221 | BO21 OutOfService | RW | ON/OFF | 21 |
| 222 | BO22 OutOfService | RW | ON/OFF | 22 |
| 223 | BO23 OutOfService | RW | ON/OFF | 23 |
| 224 | BO24 OutOfService | RW | ON/OFF | 24 |
| 225 | BO25 OutOfService | RW | ON/OFF | 25 |
| 226 | BO26 OutOfService | RW | ON/OFF | 26 |
| 227 | BO27 OutOfService | RW | ON/OFF | 27 |
| 228 | BO28 OutOfService | RW | ON/OFF | 28 |
| 229 | BO29 OutOfService | RW | ON/OFF | 29 |
| 230 | BO30 OutOfService | RW | ON/OFF | 30 |
| 231 | BO31 OutOfService | RW | ON/OFF | 31 |
| 232 | BO32 OutOfService | RW | ON/OFF | 32 |
| 233 | BO33 OutOfService | RW | ON/OFF | 33 |
| 234 | BO34 OutOfService | RW | ON/OFF | 34 |
| 235 | BO35 OutOfService | RW | ON/OFF | 35 |
| 236 | BO36 OutOfService | RW | ON/OFF | 36 |
| 237 | BO37 OutOfService | RW | ON/OFF | 37 |
| 238 | BO38 OutOfService | RW | ON/OFF | 38 |
| 239 | BO39 OutOfService | RW | ON/OFF | 39 |
| 240 | BO40 OutOfService | RW | ON/OFF | 40 |
| 241 | BO41 OutOfService | RW | ON/OFF | 41 |
| 242 | BO42 OutOfService | RW | ON/OFF | 42 |
| 243 | BO43 OutOfService | RW | ON/OFF | 43 |
| 244 | BO44 OutOfService | RW | ON/OFF | 44 |
| 245 | BO45 OutOfService | RW | ON/OFF | 45 |
| 246 | BO46 OutOfService | RW | ON/OFF | 46 |
| 247 | BO47 OutOfService | RW | ON/OFF | 47 |
| 248 | BO48 OutOfService | RW | ON/OFF | 48 |
| 249 | BO49 OutOfService | RW | ON/OFF | 49 |
| 250 | BO50 OutOfService | RW | ON/OFF | 50 |
| 251 | BO51 OutOfService | RW | ON/OFF | 51 |
| 252 | BO52 OutOfService | RW | ON/OFF | 52 |
| 253 | BO53 OutOfService | RW | ON/OFF | 53 |
| 254 | BO54 OutOfService | RW | ON/OFF | 54 |
| 255 | BO55 OutOfService | RW | ON/OFF | 55 |
| 256 | BO56 OutOfService | RW | ON/OFF | 56 |
| 257 | BO57 OutOfService | RW | ON/OFF | 57 |
| 258 | BO58 OutOfService | RW | ON/OFF | 58 |
| 259 | BO59 OutOfService | RW | ON/OFF | 59 |
| 260 | BO60 OutOfService | RW | ON/OFF | 60 |
| 261 | BO61 OutOfService | RW | ON/OFF | 61 |
| 262 | BO62 OutOfService | RW | ON/OFF | 62 |
| 263 | BO63 OutOfService | RW | ON/OFF | 63 |
| 264 | BO64 OutOfService | RW | ON/OFF | 64 |
| 265 | BO65 OutOfService | RW | ON/OFF | 65 |
| 266 | BO66 OutOfService | RW | ON/OFF | 66 |

Table 30. List of physical output registers (OutOfService).

Sample Packets

The following are examples of requests to specific groups of output registers.

Write to Output Reg201

Table 31 shows the result of a write request to output OutOfService Reg201 (Function 5 Single Write, BO1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 0F | Function | 0F |
| Register Address Hi | DB | Register Address Hi | DB |
| Register Address Lo | 00 | Register Address Lo | 00 |
| Quantity of Outputs Hi | 00 | Quantity of Outputs Hi | 00 |
| Quantity of Outputs Lo | 0A | Quantity of Outputs Lo | 0A |
| Byte Count | 02 | Packet CRC Hi |  |
| Output Value Hi | CD | Packet CRC Lo |  |
| Output Value Lo | 03 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 31. Sample packet for multiple write to output Reg220–Reg229.

Multiple Write Output Reg220–Reg229

Table 32 shows the result of a multiple write to BO OutOfService Reg220–229 (Function 15 Multiple Write, BO 20–29 in map).

Note that the Hi byte 0xCD addresses outputs 27–20, with the least-significant bit addressing the lowest output 20 and the most-significant bit addressing the highest output 27. The Lo byte 03 addresses outputs 29–28, with the least-significant bit addressing the lowest output 28. Unused bits in the last data byte are padded with zeros

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 05 | Function | 05 |
| Register Address Hi | 00 | Register Address Hi | 00 |
| Register Address Lo | C8 | Register Address Lo | C8 |
| Output Value Hi | FF | Output Value Hi | FF |
| Output Value Lo | 00 | Output Value Lo | 00 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 32. Sample packet for write to output Reg201.

## Binary Output (BO) Object – (Registers 2001 – 3260)

Each Binary Output object contains 12 properties that are exposed to MODBUS.  These object properties are writable via Function Codes 6 & 16 and readable by Function Code 3.   Writes to the BO Value occur at BACnet Priority Level 5  (Critical Equipment Control).

Table 33 shows list of registers associated with B01-B066.

| Register | BO Object | Type |
| --- | --- | --- |
| 2001 – 2018 | BO1 | RW |
| 2019 – 2036 | BO2 | RW |
| 2037 – 2054 | BO3 | RW |
| 2055 – 2072 | BO4 | RW |
| 2073 – 2090 | BO5 | RW |
| 2091 – 2108 | BO6 | RW |
| 2109 – 2126 | BO7 | RW |
| 2127 – 2144 | BO8 | RW |
| 2145 – 2162 | BO9 | RW |
| 2163 – 2180 | BO10 | RW |
| 2181 – 2198 | BO11 | RW |
| 2199 – 2216 | BO12 | RW |
| 2217 – 2234 | BO13 | RW |
| 2235 – 2252 | BO14 | RW |
| 2253 – 2270 | BO15 | RW |
| 2271 – 2288 | BO16 | RW |
| 2289 – 2306 | BO17 | RW |
| 2307 – 2324 | BO18 | RW |
| 2325 – 2342 | BO19 | RW |
| 2343 – 2360 | BO20 | RW |
| 2361 – 2378 | BO21 | RW |
| 2379 – 2396 | BO22 | RW |
| 2397 – 2414 | BO23 | RW |
| 2415 – 2432 | BO24 | RW |
| 2433 – 2450 | BO25 | RW |
| 2451 – 2468 | BO26 | RW |
| 2469 – 2486 | BO27 | RW |
| 2487 – 2504 | BO28 | RW |
| 2505 – 2522 | BO29 | RW |
| 2523 – 2540 | BO30 | RW |
| 2541 – 2558 | BO31 | RW |
| 2559 – 2576 | BO32 | RW |
| 2577 – 2594 | BO33 | RW |
| 2595 – 2612 | BO34 | RW |
| 2613 – 2630 | BO35 | RW |
| 2631 – 2648 | BO36 | RW |
| 2649 – 2666 | BO37 | RW |
| 2667 – 2684 | BO38 | RW |
| 2685 – 2702 | BO39 | RW |
| 2703 – 2720 | BO40 | RW |
| 2721 – 2738 | BO41 | RW |
| 2739 – 2756 | BO42 | RW |
| 2757 – 2774 | BO43 | RW |
| 2775 – 2792 | BO44 | RW |
| 2793 – 2810 | BO45 | RW |
| 2811 – 2828 | BO46 | RW |
| 2829 – 2846 | BO47 | RW |
| 2847 – 2864 | BO48 | RW |
| 2865 – 2882 | BO49 | RW |
| 2883 – 2900 | BO50 | RW |
| 2901 – 2918 | BO51 | RW |
| 2919 – 2936 | BO52 | RW |
| 2937 – 2954 | BO53 | RW |
| 2955 – 2972 | BO54 | RW |
| 2973 – 2990 | BO55 | RW |
| 2991 – 3008 | BO56 | RW |
| 3009 – 3026 | BO57 | RW |
| 3027 – 3044 | BO58 | RW |
| 3045 – 3062 | BO59 | RW |
| 3063 – 3080 | BO60 | RW |
| 3081 – 3098 | BO61 | RW |
| 3099 – 3116 | BO62 | RW |
| 3117 – 3134 | BO63 | RW |
| 3135 – 3152 | BO64 | RW |
| 3153 – 3170 | BO65 | RW |
| 3171 – 3188 | BO66 | RW |

Table 33. Binary Output (BO) Registers

| Offset | Modbus regs | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 2001 | Bit | OutOfService | Int | 0–1 | RW |
| 1 | 2002 | Byte | Value | Int | 0–1 | RW |
| 2 | 2003 | Bit | Commissioned | Int | 0–1 | RW |
| 3 | 2004 | Word | Reliability | Int | Enum | R |
| 4 | 2005–2006 | Dword | MinimumOffTime | Word | 0–65536 | RW |
| 6 | 2007–2008 | Dword | MinimumOnTime | Word | 0–65536 | RW |
| 8 | 2009 | Byte | DefaultValue | Word | 0–65536 | RW |
| 9 | 2010–2011 | Dword | StartDelayTime | Word | 0–65536 | RW |
| 11 | 2012 | Byte | FbackValue | Word | 0–65536 | RW |
| 12 | 2013 | Byte | FlickWarnTime | Word | 0–65536 | RW |
| 13 | 2014 | Word | FlickWarnPAEnable | Int | On/Off | RW |
| 14 | 2015 | Word | OverrideTime | Word | 0–65536 | RW |

Table 34. Address space of binary output registers.

Binary Output (BO) Properties:

Each Binary Output (BO) object exposes the following object properties (Table 34).

Sample Packets

Following are examples of function requests to binary output registers.

Read All BO1 Properties

Table.35 is an example of a read of all BO1 properties: OutOfService, Value, Commissioned, Reliability and MinimumOffTime Reg2001–Reg2006 (Function 3, BO1in map).

| Request | Response |
| --- | --- |
| Field Name | Hex |
| Device Address | 01 | Field Name | Hex |
| Function | 03 | Device Address | 01 |
| Register Address Hi | 00 | Function | 03 |
| Register Address Lo | 00 | Byte Count | 0C |
| Registers Hi | 00 | Register Value Hi (2001) | 00 |
| Registers Lo | 06 | Register Value Lo (2001) | 00 |
| Packet CRC Hi |  | Register Value Hi (2002) | 00 |
| Packet CRC Lo |  | Register Value Lo (2002) | 01 |
|  |  | Register Value Hi (2003) | 00 |
|  |  | Register Value Lo (2003) | 00 |
|  |  | Register Value Hi (2004) | 00 |
|  |  | Register Value Lo (2004) | 00 |
|  |  | Register Value Hi (2005) | 00 |
|  |  | Register Value Lo (2005) | 00 |
|  |  | Register Value Hi (2006) | 00 |
|  |  | Register Value Lo (2006) | 3C |
|  |  | Packet CRC Hi |  |

Table 35. Sample packets for read of all BO1 properties.

The response is as follows:

Reg2001 (OutOfService): 0x0000, FALSE,

Reg2002 (Value): 0x0001, ON

Reg2003 (Commissioned): 0x000, FALSE

Reg2004 (Reliability): 0x0000, Normal,

Reg2005 (MinimumOffTime): 0x0003C, 60sec

Single Write to BO1 Override Time

Table.36 is an example of a single write of 5 minutes (0x0005) to BO1 Override Time Reg.2015 (Function 6, BO1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 06 | Function | 06 |
| Register Address Hi | 07 | Register Address Hi | 07 |
| Register Address Lo | DE | Register Address Lo | DE |
| Registers Hi | 00 | Registers Hi | 00 |
| Registers Lo | 05 | Registers Lo | 05 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 36. Sample packets for single write to BO1 overwrite time.

Multiple Write to Binary Output

Table.37 is an example of a multiple write to BO OutOfService and Value 1–3 (Function 16, BO 1in map). This example writes OutOfService to TRUE and Value to 0x0000 (OFF).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 10 | Function | 10 |
| Register Address Hi | 07 | Register Address Hi | 00 |
| Register Address Lo | D0 | Register Address Lo | 00 |
| Registers Hi | 00 | Registers Hi | 00 |
| Registers Lo | 02 | Registers Lo | 02 |
| Register Value 1 Hi | 00 | Packet CRC Hi |  |
| Register Value 1 Lo | 01 | Packet CRC Lo |  |
| Register Value 2 Hi | 00 |  |  |
| Register Value 2 Lo | 00 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 37. Sample packets for multiple write to binary output.

Feedback Registers

The feedback value of the Binary outputs(BO) is mapped starting at Modbus register 1 and are read by function code 02. Actual value (Feedback) registers start at 1, are read by Function Code 02, and are mapped to Binary Outputs 1–66. Note that the value of each register is the combined value of the current feedback input value and the current command of that output. A bit value of 0 represents the feedback OFF and a 1 represents the Feedback ON.

The feedback registers are listed in Table 38.

| Reg. | Contents | Type | Format | BO Instance |
| --- | --- | --- | --- | --- |
| 1 | BO1 Feedback | R | Bit | 01 |
| 2 | BO2 Feedback | R | Bit | 02 |
| 3 | BO3 Feedback | R | Bit | 03 |
| 4 | BO4 Feedback | R | Bit | 04 |
| 5 | BO5 Feedback | R | Bit | 05 |
| 6 | BO6 Feedback | R | Bit | 06 |
| 7 | BO7 Feedback | R | Bit | 07 |
| 8 | BO8 Feedback | R | Bit | 08 |
| 9 | BO9 Feedback | R | Bit | 09 |
| 10 | BO10 Feedback | R | Bit | 10 |
| 11 | BO11 Feedback | R | Bit | 11 |
| 12 | BO12 Feedback | R | Bit | 12 |
| 13 | BO13 Feedback | R | Bit | 13 |
| 14 | BO14 Feedback | R | Bit | 14 |
| 15 | BO15 Feedback | R | Bit | 15 |
| 16 | BO16 Feedback | R | Bit | 16 |
| 17 | BO17 Feedback | R | Bit | 17 |
| 18 | BO18 Feedback | R | Bit | 18 |
| 19 | BO19 Feedback | R | Bit | 19 |
| 20 | BO20 Feedback | R | Bit | 20 |
| 21 | BO21 Feedback | R | Bit | 21 |
| 22 | BO22 Feedback | R | Bit | 22 |
| 23 | BO23 Feedback | R | Bit | 23 |
| 24 | BO24 Feedback | R | Bit | 24 |
| 25 | BO25 Feedback | R | Bit | 25 |
| 26 | BO26 Feedback | R | Bit | 26 |
| 27 | BO27 Feedback | R | Bit | 27 |
| 28 | BO28 Feedback | R | Bit | 28 |
| 29 | BO29 Feedback | R | Bit | 29 |
| 30 | BO30 Feedback | R | Bit | 30 |
| 31 | BO31 Feedback | R | Bit | 31 |
| 32 | BO32 Feedback | R | Bit | 32 |
| 33 | BO33 Feedback | R | Bit | 33 |
| 34 | BO34 Feedback | R | Bit | 34 |
| 35 | BO35 Feedback | R | Bit | 35 |
| 36 | BO36 Feedback | R | Bit | 36 |
| 37 | BO37 Feedback | R | Bit | 37 |
| 38 | BO38 Feedback | R | Bit | 38 |
| 39 | BO39 Feedback | R | Bit | 39 |
| 40 | BO40 Feedback | R | Bit | 40 |
| 41 | BO41 Feedback | R | Bit | 41 |
| 42 | BO42 Feedback | R | Bit | 42 |
| 43 | BO43 Feedback | R | Bit | 43 |
| 44 | BO44 Feedback | R | Bit | 44 |
| 45 | BO45 Feedback | R | Bit | 45 |
| 46 | BO46 Feedback | R | Bit | 46 |
| 47 | BO47 Feedback | R | Bit | 47 |
| 48 | BO48 Feedback | R | Bit | 48 |
| 49 | BO49 Feedback | R | Bit | 49 |
| 50 | BO50 Feedback | R | Bit | 50 |
| 51 | BO51 Feedback | R | Bit | 51 |
| 52 | BO52 Feedback | R | Bit | 52 |
| 53 | BO53 Feedback | R | Bit | 53 |
| 54 | BO54 Feedback | R | Bit | 54 |
| 55 | BO55 Feedback | R | Bit | 55 |
| 56 | BO56 Feedback | R | Bit | 56 |
| 57 | BO57 Feedback | R | Bit | 57 |
| 58 | BO58 Feedback | R | Bit | 58 |
| 59 | BO59 Feedback | R | Bit | 59 |
| 60 | BO60 Feedback | R | Bit | 60 |
| 61 | BO61 Feedback | R | Bit | 61 |
| 62 | BO62 Feedback | R | Bit | 62 |
| 63 | BO63 Feedback | R | Bit | 63 |
| 64 | BO64 Feedback | R | Bit | 64 |
| 65 | BO65 Feedback | R | Bit | 65 |
| 66 | BO66 Feedback | R | Bit | 66 |

Table 38. List of feedback registers.

Sample Packets

Table 39 is an example of a request to read for output Feedback instances 1–19 (Function 2, BO 1–19 in map).

Note that the feedback status of inputs 8–1 is shown as the byte value 0xAC or binary 1010 1100. Input 8 is the MSB of this byte and input 1 is the LSB. The feedback status input 19–17 is shown as the byte value 0x06 or binary 0000 0110. Input 19 is the third bit position from the left and input 17 is the LSB.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 02 | Function | 0F |
| Register Address Hi | 00 | Byte Count | 03 |
| Register Address Lo | 00 | Input Status 8–1 | AC |
| Quantity of Inputs Hi | 00 | Input Status 16–9 | DB |
| Quantity of Inputs Lo | 0A | Input Status 19–17 | 06 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 39. Sample packets for output feedback instances 1–19.

Special Registers

In addition to the 66 breaker outputs, the lighting controller has several special outputs (Table 40) to control other features on the main board.

These special outputs are mapped to MODBUS coil registers 67-70 and are accessed by function code 01/05/15.

Note: These outputs are not for general use. Don’t write to these registers without detailed knowledge of their purpose, operation and possible consequences.

| Reg | Contents | Units / Range | Type |
| --- | --- | --- | --- |
| 67 | [BO67] – Output Sweep | On/Off | R/W |
| 68 | [BO68] - Device Alarm Status | On/Off | R/W |
| 69 | [BO69] - Voltage Input | On/Off | R/W |
| 70 | [BO70] - MSP430 Reset | On/Off | R/W |

Table 40.Special output Registers

## Sample packets

The following are samples of packets generated by requests for specific groups of outputs.

Read BO Registers 67 to 70

Table 41 is an example of a request to read BO67-BO70 (Function 1, BO67 – O70).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 00 | Byte Count | 01 |
| Register Address Lo | 42 | Outputs Status 70 – 67 | 0E |
| Quantity of Outputs Hi | 00 | Packet CRC Hi |  |
| Quantity of Outputs Lo | 04 | Packet CRC Lo |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 41. Request to read BO67-BO70

Write “On” to output Value Reg67 (Function 5 Single Write, BO67 in map). Table 42 is an example of a single write to BO67.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 05 | Function | 05 |
| Register Address Hi | 00 | Register Address Hi | 00 |
| Register Address Lo | 42 | Register Address Lo | 42 |
| Output Value Hi | FF | Output Value Hi | FF |
| Output Value Lo | 00 | Output Value Lo | 00 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 42. Request to write  Register 67

Lighting Group Objects

Individual binary outputs can be grouped together to represent the logical layout of a building installation. Sixteen lighting groups (LG) are available and each one can contain a group of 33 outputs.

Lighting Group Output Registers (Coils)

Actual value registers start at 301. The Lighting Group and OutOfService property can be commanded by Function Code 05 and 15 and read by Function Code 1 and are mapped to Lighting Group Instances 1–16. The value in the register represents the Lighting Group’s PresentValue.

The Lighting Group output registers are listed inTable 43.

| Reg. | Contents | Type | Format | Instance |
| --- | --- | --- | --- | --- |
| 301 | LG01 Value | RW | On/Off | 01 |
| 302 | LG02 Value | RW | On/Off | 02 |
| 303 | LG03 Value | RW | On/Off | 03 |
| 304 | LG04 Value | RW | On/Off | 04 |
| 305 | LG05 Value | RW | On/Off | 05 |
| 306 | LG06 Value | RW | On/Off | 06 |
| 307 | LG07 Value | RW | On/Off | 07 |
| 308 | LG08 Value | RW | On/Off | 08 |
| 309 | LG09 Value | RW | On/Off | 09 |
| 310 | LG10 Value | RW | On/Off | 10 |
| 311 | LG11 Value | RW | On/Off | 11 |
| 312 | LG12 Value | RW | On/Off | 12 |
| 313 | LG13 Value | RW | On/Off | 13 |
| 314 | LG14 Value | RW | On/Off | 14 |
| 315 | LG15 Value | RW | On/Off | 15 |
| 316 | LG16 Value | RW | On/Off | 16 |

Table 43. Lighting Group output registers.

Sample Packets

Table44 is an example of a request for LG Value Reg302 to Reg305 (Function Code 1, LG2 – LG5 in map).

Note that the status of outputs 5–2 is hex 0B or binary 0000 1011, where LG302 is the LSB and LG305 is the fourth bit from the left. Unused bits are padded as zero.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 01 | Byte Count | 01 |
| Register Address Lo | 2D | Output Status 5–2 | 0B |
| Quantity of LG Hi | 00 | Packet CRC Hi |  |
| Quantity of LG Lo | 04 | Packet CRC Lo |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 44. Sample packets for LG Value Reg302 to Reg305.

Lighting Group Registers (OutOfService)

The Lighting Group OutOfService registers are listed in Table45.

| Reg. | Contents | Type | Format | Instance |
| --- | --- | --- | --- | --- |
| 401 | LG01 OutOfService | RW | On/Off | 01 |
| 402 | LG02 OutOfService | RW | On/Off | 02 |
| 403 | LG03 OutOfService | RW | On/Off | 03 |
| 404 | LG04 OutOfService | RW | On/Off | 04 |
| 405 | LG05 OutOfService | RW | On/Off | 05 |
| 406 | LG06 OutOfService | RW | On/Off | 06 |
| 407 | LG07 OutOfService | RW | On/Off | 07 |
| 408 | LG08 OutOfService | RW | On/Off | 08 |
| 409 | LG09 OutOfService | RW | On/Off | 09 |
| 410 | LG10 OutOfService | RW | On/Off | 10 |
| 411 | LG11 OutOfService | RW | On/Off | 11 |
| 412 | LG12 OutOfService | RW | On/Off | 12 |
| 413 | LG13 OutOfService | RW | On/Off | 13 |
| 414 | LG14 OutOfService | RW | On/Off | 14 |
| 415 | LG15 OutOfService | RW | On/Off | 15 |
| 416 | LG16 OutOfService | RW | On/Off | 16 |

Table 45. Lighting Group OutOfService registers.

Sample Packets

Table 46 is an example of a request for LG OutOfService status instance 401–416 (Function Code 1, LG1–16 in map).

Note that the LG OutOfService Status of 408–401 is shown as hex AB or binary 1010 1011, where LG 401 is the LSB and LG408 is the MSB.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 01 | Byte Count | 02 |
| Register Address Lo | 90 | OutOfService Reg408–401 | AB |
| Quantity of LG Hi | 00 | OutOfService Reg416–409 | AA |
| Quantity of LG Lo | 10 | Packet CRC Hi |  |
| Packet CRC Hi |  | Packet CRC Lo |  |
| Packet CRC Lo |  |  |  |

Table 46. Sample packets for LG out of Service instance 401–416.

Lighting Group Setup Registers

The Lighting Group setup parameters are assigned a block of holding registers starting at 4001 as indicated in table 47. Lighting Group properties can be commanded by Function Code 06 and 16 and read by Function 3. Write to LG value is at priority level 1 by default.

Note that any reference in this object that does not exist is shown as 0xFFFF in all three registers. To delete a reference, write 0x0000 to all three registers. The same applies to deleting an entry in any of the two arrays in this object. Lighting Outputs and Common Group entries are sorted in object execution time. Therefore, multiple entries can only be deleted in one write.

The template shown in table 48 is repeated 16 times in this assigned space.

| Register | LG Object | Type |  | Register | BO Object | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 4001 – 4363 | LG1 | RW |  | 6905 – 7267 | LG9 | RW |
| 4364 – 4726 | LG2 | RW |  | 7268 – 7630 | LG10 | RW |
| 4727 – 5089 | LG3 | RW |  | 7631 – 7993 | LG11 | RW |
| 5090 – 5452 | LG4 | RW |  | 7994 – 8356 | LG12 | RW |
| 5453 – 5815 | LG5 | RW |  | 8357 – 8719 | LG13 | RW |
| 5816 – 6179 | LG6 | RW |  | 8720 – 9082 | LG14 | RW |
| 6179 – 6542 | LG7 | RW |  | 9083 – 9445 | LG15 | RW |
| 6542 – 6904 | LG8 | RW |  | 9446 – 9808 | LG16 | RW |

Table 47 different lighting group registers

| Offset | Modbus #regs | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 4001 | BYTE | Out of Service | Int | 0 – 1 | RW |
| 1 | 4002 | BYTE | Value * | Int | 0 – 1 | RW |
| 2 | 4003 | BYTE | Current Priority | Int | Enum (1 – 6) | R |
| 3 | 4004 | WORD | Reliability | Int | Enum | R |
|  |  |  | Override Reference |  |  |  |
| 4 | 4005 |  | Panel Number | Int | 0 – 99 | RW |
| 5 | 4006 |  | Object Type | Int | 0 – 65535 BI= 3 BV= 5 | RW |
| 6 | 4007 |  | Object Instance | Word | 1 – 65535 | RW |
| 7 | 4008 | WORD | Override Time | WORD | 0 – 65535 | RW |
|  |  |  | Photocell Reference |  |  |  |
| 8 | 4009 |  | Panel Number | Word | 0 – 99 | RW |
| 9 | 4010 |  | Object Type | Int | 0 – 65535 AI= 0 AV= 2 BI= 3 MI= 13 | RW |
| 10 | 4011 |  | Object Instance | Word | 1 – 65535 | RW |
| 11 | 4012 – 4013 |  | Photocell On Val | WORD | 0 – 65535 | RW |
| 13 | 4014 – 4015 |  | Photocell Off Val | WORD | 0 – 65535 | RW |
| 15 | 4016 |  | Photocell On Enable | Int | On/Off | RW |
| 16 | 4017 |  | Photocell Off Enable | Int | On/Off | RW |
|  |  |  | Schedule Reference |  |  |  |
| 17 | 4018 |  | Panel Number | Int | 0 – 99 | RW |
| 18 | 4019 |  | Object Type | Int | 0 – 65535 BV= 5 SCH= 17 | RW |
| 19 | 4020 |  | Instance | Word | 1 – 65535 | RW |
| 20 | 4021 |  | Schedule Off | Int | On/Off | RW |
| 21 | 4022 |  | Schedule On | Int | On/Off | RW |
| 22 | 4023 |  | Astro On Enable | Int | On/Off | RW |
| 23 | 4024 |  | Astro Off Enable | Int | On/Off | RW |
| 24 | 4025 | BYTE | Astro On Offset | Int | 0 – 254 | RW |
| 25 | 4026 | LONG | Astro On Calc Hi** | Word | 0 – 254 | R |
| 26 | 4027 |  | Astro On Calc Lo** | Word | 0 – 254 | R |
| 27 | 4028 | BYTE | Astro Off Offset | Int | 0 – 254 | RW |
| 28 | 4029 | LONG | Astro Off Calc Hi** | Word | 0 – 254 | R |
| 29 | 4030 |  | Astro Off Calc Lo** | Word | 0 – 254 | R |
| 30 | 4031 | BYTE | FlickWarnEnable | Word | 1-On / 0-Off | RW |
| 31 | 4032 | BYTE | FlickWarnTime | Word | 0 – 240 min | RW |
| 32 | 4033 | WORD | FlickWarnPAEnble | Word | 0 – 65535 | RW |
| 33 | 4034 | WORD | FlickWarnInputEnb | Word | 0 – 65535 | RW |
|  |  | Array of 33 Output Ref/ Switch Ref pairs | Lighting Outputs |  |  |  |
|  |  |  | Output Ref |  |  |  |
| 34 | 4035 |  | Panel Number | Word | 1 – 99 | RW |
| 35 | 4036 |  | Object Type |  | 4 – [BO] 303 – [LG] | RW |
| 36 | 4037 |  | Object Instance | Word | 1 – 65535 | RW |
|  |  |  | Switch Ref |  |  |  |
| 37 | 4038 |  | Panel Number | Word | 1 – 99 | RW |
| 38 | 4039 |  | Object Type |  | 3 – [BI] 13 – [MI] | RW |
| 39 | 4040 |  | Object Instance | Word | 0 – 65535 | RW |
| 40 | 4041 |  | Value | Word |  | RW |
| 41 | 4042 |  | Switch Value | Word |  | RW |
| 42 | 4043 – 4298 |  | 32 more entries: 8 registers per entry |  |  | RW |
| 298 | 4299 |  | Common Off Time | Int | 0 – 1000 | RW |
|  |  | Array of 16 | Common Groups |  |  |  |
| 299 | 4300 |  | Panel Number | Word | 1 – 99 | RW |
| 300 | 4301 |  | Object Type | Word | 303 – [LG] | RW |
| 301 | 4302 |  | Object Instance | Word | 1 – 16 | RW |
| 302 | 4303 |  | Value | Word |  | RW |
| 303 | 4304 – 4363 |  | 15 remote LG refs: 4 registers per entry |  |  | RW |
|  |  |  | 363 registers / LG |  |  |  |

Table 48. Lighting Group setup registers.

Sample Packets

The following are examples of requests to specific setup registers.

Read for LG1 OutOfService Value

Table 49 is an example of read for LG1 OutOfService, Value and Current Priority for Reg4001–Reg4003 (Function 3, LG 1in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 0F | Byte Count | 06 |
| Register Address Lo | A0 | Register Value Hi (4001) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (4001) | 00 |
| No. of Registers Lo | 03 | Register Value Hi (4002) | 00 |
| Packet CRC Hi |  | Register Value Lo (4002) | 02 |
| Packet CRC Lo |  | Register Value Hi (4003) | 00 |
|  |  | Register Value Lo (4003) | 06 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 49. Sample packets for read for Reg4001–Reg4003.

Response is as follows:

Reg4001 (OutOfService) 0x0000 – FALSE,

Reg4002 (Value) 0x0002 – Override

Reg4003 (Current Priority) 0x0006 – Priority 6

Read LG Photocell Reference

Table 50 is an example of read LG Photocell Reference (Object Type, Object Instance and Panel Number) for Reg. 4009–Reg4011 (Function 3, LG1 in map).

The response is Photocell Reference Object Type 1 (AI), Object Instance 2, Panel Number 100.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 0F | Byte Count | 06 |
| Register Address Lo | A8 | Register Value Hi (4009) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (4009) | 64 |
| No. of Registers Lo | 03 | Register Value Hi (4010) | 00 |
| Packet CRC Hi |  | Register Value Lo (4010) | 00 |
| Packet CRC Lo |  | Register Value Hi (4011) | 00 |
|  |  | Register Value Lo (4011) | 02 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 50. Sample packets for read LG photocell reference for Reg4009–4011.

Read Lighting Output Array

Table 51 is an example of read Lighting Output Array Entry 2 Reg4035–Reg4042 (Function 3, LG1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 0F | Byte Count | 10 |
| Register Address Lo | C2 | Register Value Hi (4035) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (4035) | 64 |
| No. of Registers Lo | 08 | Register Value Hi (4036) | 00 |
| Packet CRC Hi |  | Register Value Lo (4036) | 04 |
| Packet CRC Lo |  | Register Value Hi (4037) | 00 |
|  |  | Register Value Lo (4037) | 02 |
|  |  | Register Value Hi (4038) | 00 |
|  |  | Register Value Lo (4038) | 64 |
|  |  | Register Value Hi (4039) | 00 |
|  |  | Register Value Lo (4039) | 0D |
|  |  | Register Value Hi (4040) | 00 |
|  |  | Register Value Lo (4040) | 66 |
|  |  | Register Value Hi (4041) | 00 |
|  |  | Register Value Lo (4041) | 00 |
|  |  | Register Value Hi (4042) | 00 |
|  |  | Register Value Lo (4042) | 02 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 51. Sample packets for read for lighting output array.

The response to reading Array Index 2 of Lighting Output, which consists of Output Reference and Switch Reference, is as follows:

Reg4035–Reg3037 Output Reference object: 0x006400040002 - 100.BO2

Reg4038–Reg4040 Switch Reference object: 0x0063000E0065 - 100.MI101

Reg4041 Reference Value: 00000

Reg4042 Switch Value: 0002

Single Write OFF to Lighting Group 1

Table 52 is an example of a single write OFF (0x0000) to LG1 Value Reg4002  (Function 6, LG 1in map). Note that OutOfService is automatically set to TRUE with this write.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 06 | Function | 06 |
| Register Address Hi | 0B | Register Address Hi | 0B |
| Register Address Lo | B9 | Register Address Lo | B9 |
| Register Value Hi | 00 | Register Value Hi | 00 |
| Register Value Lo | 00 | Register Value Lo | 00 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 52. Sample packets for single write OFF to LG 1.

Read for Lighting Group 1 OutOfService

Table 53 is an example of a read for LG1 OutOfService, Value and Current Priority, Reg4001–Reg4003. This is the result after the single write of the previous example.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 0B | Byte Count | 06 |
| Register Address Lo | B8 | Register Value Hi (4001) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (4001) | 01 |
| No. of Registers Lo | 03 | Register Value Hi (4002) | 00 |
| Packet CRC Hi |  | Register Value Lo (4002) | 01 |
| Packet CRC Lo |  | Register Value Hi (4003) | 00 |
|  |  | Register Value Lo (4003) | 01 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 53. Sample packet for read of LG1 OutOfService.

The response is as follows:

Reg4001 (OutOfService) 0x0001: TRUE

Reg4002 (Value) 0x0001: On

Reg4003 (Current Priority) 0x0001: Priority 1 (Manual Override)

Single Write to Restore OutOfService

Table 54 is an example of a single write to restore the OutOfService to FALSE. We do a write to LG present value with 0x04 (Reg4002).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 06 | Function | 06 |
| Register Address Hi | 0B | Register Address Hi | 0B |
| Register Address Lo | B9 | Register Address Lo | B9 |
| Register Value Hi | 00 | Register Value Hi | 00 |
| Register Value Lo | 04 | Register Value Lo | 04 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 54. Sample packets for single write to restore OutOfService.

Read for LG1 OutOfService

Table 55 is an example of a read for LG1 OutOfService, Value and Current Priority, Reg4001–Reg4003. This is the result after the single write of the previous example.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 0B | Byte Count | 06 |
| Register Address Lo | B8 | Register Value Hi (4001) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (4001) | 01 |
| No. of Registers Lo | 03 | Register Value Hi (4002) | 00 |
| Packet CRC Hi |  | Register Value Lo (4002) | 02 |
| Packet CRC Lo |  | Register Value Hi (4003) | 00 |
|  |  | Register Value Lo (4003) | 06 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 55. Sample packets for read for LG1 OutOfService.

The response is as follows:

Reg4001 (OutOfService) 0x0000: FALSE

Reg4002 (Value) 0x0002: Overwrite

Reg4003 (Current Priority) 0x0006: Priority 1 (Default Value)

Schedule

The Controller contains 16 schedule objects that is written by the Modbus Master. The Schedule Event value and OutOfService property can be commanded by Function Codes 05 and 15 and read by Function Code 1.

Schedule Value Registers

The Schedule value registers are listed in Table 56.

| Reg. | Contents | Type | Format | Instance |
| --- | --- | --- | --- | --- |
| 501 | SCH01 Value | RW | On/Off | 01 |
| 502 | SCH02 Value | RW | On/Off | 02 |
| 503 | SCH03 Value | RW | On/Off | 03 |
| 504 | SCH04 Value | RW | On/Off | 04 |
| 505 | SCH05 Value | RW | On/Off | 05 |
| 506 | SCH06 Value | RW | On/Off | 06 |
| 507 | SCH07 Value | RW | On/Off | 07 |
| 508 | SCH08 Value | RW | On/Off | 08 |
| 509 | SCH09 Value | RW | On/Off | 09 |
| 510 | SCH10 Value | RW | On/Off | 10 |
| 511 | SCH11 Value | RW | On/Off | 11 |
| 512 | SCH12 Value | RW | On/Off | 12 |
| 513 | SCH13 Value | RW | On/Off | 13 |
| 514 | SCH14 Value | RW | On/Off | 14 |
| 515 | SCH15 Value | RW | On/Off | 15 |
| 516 | SCH16 Value | RW | On/Off | 16 |

Table 56. Schedule value registers.

Sample Packets

Table 57 is an example of a request for SCH Value Reg501–Reg505 (Function 1, SCH1–5 in map). Note that SCH Value Status Reg505–501 (SCH05–SCH01) is shown as hex value 1F or binary 0001 1111, while Reg501 is the LSB and Reg505 is the fifth bit from the left.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 01 | Byte Count | 01 |
| Register Address Lo | F4 | SCH OutOfService 505–501 | 1F |
| Quantity of SCH Hi | 00 | Packet CRC Hi |  |
| Quantity of SCH Lo | 05 | Packet CRC Lo |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 57. Sample packets for request for SCH Value.

Schedule OutOfService Registers

The Schedule OutOfService registers are listed in Table 58.

| Reg. | Contents | Type | Format | Instance |
| --- | --- | --- | --- | --- |
| 601 | SCH01 OutOfService | RW | On/Off | 01 |
| 602 | SCH02 OutOfService | RW | On/Off | 02 |
| 603 | SCH03 OutOfService | RW | On/Off | 03 |
| 604 | SCH04 OutOfService | RW | On/Off | 04 |
| 605 | SCH05 OutOfService | RW | On/Off | 05 |
| 606 | SCH06 OutOfService | RW | On/Off | 06 |
| 607 | SCH07 OutOfService | RW | On/Off | 07 |
| 608 | SCH08 OutOfService | RW | On/Off | 08 |
| 609 | SCH09 OutOfService | RW | On/Off | 09 |
| 610 | SCH10 OutOfService | RW | On/Off | 10 |
| 611 | SCH11 OutOfService | RW | On/Off | 11 |
| 612 | SCH12 OutOfService | RW | On/Off | 12 |
| 613 | SCH13 OutOfService | RW | On/Off | 13 |
| 614 | SCH14 OutOfService | RW | On/Off | 14 |
| 615 | SCH15 OutOfService | RW | On/Off | 15 |
| 616 | SCH16 OutOfService | RW | On/Off | 16 |

Table 58. Schedule OutOfService registers.

Sample Packets

Table 59 is an example of a request for SCH OutOfService status instance Reg601–Reg616 (Function 1, SCH1–16 in map). Note that SCH OutOfService Status Reg4208– Reg4201 is shown as hex value AB or binary 1010 1011, while Reg4201 is the LSB and Reg4208 is the MSB. Reg4201 is SCH01 OutOfService Status.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 01 | Function | 01 |
| Register Address Hi | 02 | Byte Count | 02 |
| Register Address Lo | 58 | SCH OutOfService 608–601 | AB |
| Quantity of SCH Hi | 00 | SCH OutOfService 616–609 | AA |
| Quantity of SCH Lo | 10 | Packet CRC Hi |  |
| Packet CRC Hi |  | Packet CRC Lo |  |
| Packet CRC Lo |  |  |  |

Table 59. Sample packets for request for SCH OutOfService status.

Schedule Objects

Each schedule object has a block of registers that are used to maintain the schedule.

The first object starts at register address 20001 and the second object starts at 20291. Table60 indicates the list of schedule objects and their associated registers.Each day has eight pairs of ON/OFF times. Day 1 represents Monday, Day 7 represents Sunday, and Day 8 & 9 represents Calendar day(s). If a day has fewer than eight pairs, all empty pairs are filled with 0xFFFF on its ON/OFF time. Schedule properties can be edited with function code 06 and 16 and read with function code 3. Due to constraints in the code, you can only remove an entry by writing 0xFFFF with function code 06.

| Register | SCH Object | Type |  | Register | SCH Object | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 20001 – 20290 | SCH1 | RW |  | 22321 – 22610 | SCH9 | RW |
| 20291 – 20580 | SCH2 | RW |  | 22611 – 22900 | SCH10 | RW |
| 20581 – 20870 | SCH3 | RW |  | 22901 – 23190 | SCH11 | RW |
| 20871 – 21160 | SCH4 | RW |  | 23191 – 23480 | SCH12 | RW |
| 21161 – 24450 | SCH5 | RW |  | 23481 – 23770 | SCH13 | RW |
| 21451 – 21740 | SCH6 | RW |  | 23771 – 24060 | SCH14 | RW |
| 21741 – 22030 | SCH7 | RW |  | 24061 – 24350 | SCH15 | RW |
| 22031 – 22320 | SCH8 | RW |  | 24351 – 24640 | SCH16 | RW |

Table 60. Schedule Registers

Note that the first entry of each day’s time slot has to be 00:00 to indicate midnight and the time slot’s value can be changed but not its time. To schedule 24 hours ON, only one entry is needed; set the midnight value to 0x0001 and it will be turned OFF at midnight the next day. To delete an entry, fill the time and value with 0xFFFF. Only one entry can be deleted at a time. You cannot delete all entries with one write.

Configuration properties are in sets for each Schedule and have the address space shown in Table 61. Each object has 290 registers and there are 16 objects per panel.

| Offset | Modbus Reg. | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 20001 | Byte | OutOfService | Int | 0–1 | RW |
| 1 | 20002 | Byte | Value | Int | 0–1 | RW |
| Start Schedule List |
| 2 | 20003 | Byte | Day 1 Entry 1: Time Value | Int | 00:00–23:59 | RW |
| 3 | 20004 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 4 | 20005 | Byte | Day 1 Entry 2: Time Value | Int | 00:00–23:59 | RW |
| 5 | 20006 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 6 | 20007 | Byte | Day 1 Entry 3: Time Value | Int | 00:00–24:00 | RW |
| 7 | 20008 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 8 | 20009 | Byte | Day 1 Entry 4: Time Value | Int | 00:00–23:59 | RW |
| 9 | 20010 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 10 | 20011 | Byte | Day 1 Entry 5: Time Value | Int | 00:00–24:00 | RW |
| 11 | 20012 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 12 | 20013 | Byte | Day 1 Entry 6: Time Value | Int | 00:00–23:59 | RW |
| 13 | 20014 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 14 | 20015 | Byte | Day 1 Entry 7: Time Value | Int | 00:00–24:00 | RW |
| 15 | 20016 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 16 | 20017 | Byte | Day 1 Entry 8: Time Value | Int | 00:00–23:59 | RW |
| 17 | 20018 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 18 | 20019 | Byte | Day 1 Entry 9: Time Value | Int | 00:00–24:00 | RW |
| 19 | 20020 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 20 | 20021 | Byte | Day 1 Entry 10: Time Value | Int | 00:00–23:59 | RW |
| 21 | 20022 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 22 | 20023 | Byte | Day 1 Entry 11: Time Value | Int | 00:00–24:00 | RW |
| 23 | 20024 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 24 | 20025 | Byte | Day 1 Entry 12: Time Value | Int | 00:00–23:59 | RW |
| 25 | 20026 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 26 | 20027 | Byte | Day 1 Entry 13: Time Value | Int | 00:00–24:00 | RW |
| 27 | 20028 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 28 | 20029 | Byte | Day 1 Entry 14: Time Value | Int | 00:00–23:59 | RW |
| 29 | 20030 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 30 | 20031 | Byte | Day 1 Entry 15: Time Value | Int | 00:00–24:00 | RW |
| 31 | 20032 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 32 | 20033 | Byte | Day 1 Entry 16: Time Value | Int | 00:00–23:59 | RW |
| 33 | 20034 | Byte |  | Int | 0 – Off, 1 – On | RW |
| 34–289 | 20035–20290 |  | 32 Reg. per day 9 days = 288 Regs (2 for Exceptions – CALs) |  |  |  |

Table 61. Schedule object registers.

Sample Packets

The following are examples of function requests to specific registers.

Read for Schedule OutOfService

Table 62 is an example of a read for SCH OutOfService, Value and Day 1 Entry 1, Reg20001–Reg20004 (Function 3, SCH1in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 4E | Byte Count | 06 |
| Register Address Lo | 20 | Register Value Hi (20001) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (20001) | 00 |
| No. of Registers Lo | 04 | Register Value Hi (20002) | 00 |
| Packet CRC Hi |  | Register Value Lo (20002) | 01 |
| Packet CRC Lo |  | Register Value Hi (20003) | 00 |
|  |  | Register Value Lo (20003) | 00 |
|  |  | Register Value Hi (20004) | 00 |
|  |  | Register Value Lo (20004) | 00 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 62. Sample packets for read of Schedule OutOfService.

The response is as follows:

Reg20001 (OutOfService): 0x0000, FALSE

Reg20002 (Value): 0x0001, ON

Reg20003 (Entry 1, Time): 0x0000, 00:00am

Reg20004 (Entry 1, Value): 0x0000, Off Time

Read for Schedule On and Off Times

Table 63 is an example of a read for SCH Day1 (Monday) Entry 2 OnTime and OffTime Reg20005–Reg20008 (Function 3, SCH1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 4E | Byte Count | 08 |
| Register Address Lo | 23 | Register Value Hi (20005) | 05 |
| No. of Registers Hi | 00 | Register Value Lo (20005) | 00 |
| No. of Registers Lo | 04 | Register Value Hi (20006) | 00 |
| Packet CRC Hi |  | Register Value Lo (20006) | 01 |
| Packet CRC Lo |  | Register Value Hi (20007) | 06 |
|  |  | Register Value Lo (20007) | 0F |
|  |  | Register Value Hi (20008) | 00 |
|  |  | Register Value Lo (20008) | 00 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 63. Sample packets for read of Schedule On and Off times.

The response is as follows:

Reg20005–20006: 0x0500, 5:00am; 0x0001, On time

Reg20007–20008: 0x060F, 6:15am; 0x0000, Off time

Read for Schedule Day Entries

Table 64 is an example of a read for SCH Day1 (Monday), all eight entries Reg20003–Reg20034 (Function 3, SCH1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 4E | Byte Count | 40 |
| Register Address Lo | 22 | Register Value Hi (20003) | 00 |
| No. of Registers Hi | 00 | Register Value Lo (20003) | 00 |
| No. of Registers Lo | 20 | Register Value Hi (20004) | 00 |
| Packet CRC Hi |  | Register Value Lo (20004) | 00 |
| Packet CRC Lo |  | Register Value Hi (20005) | 05 |
|  |  | Register Value Lo (20005) | 00 |
|  |  | Register Value Hi (20006) | 00 |
|  |  | Register Value Lo (20006) | 01 |
|  |  | Register Value Hi (20007) | 06 |
|  |  | Register Value Lo (20007) | 0F |
|  |  | Register Value Hi (20008) | 00 |
|  |  | Register Value Lo (20008) | 00 |
|  |  | Register Value Hi (20009) | 07 |
|  |  | Register Value Lo (20009) | 0F |
|  |  | Register Value Hi (20010) | 00 |
|  |  | Register Value Lo (20010) | 01 |
|  |  | Register Value Hi (20011) | 09 |
|  |  | Register Value Lo (20011) | 00 |
|  |  | Register Value Hi (20012) | 00 |
|  |  | Register Value Lo (20012) | 00 |
|  |  | Register Value Hi (20013) | 0A |
|  |  | Register Value Lo (20013) | 1E |
|  |  | Register Value Hi (20014) | 00 |
|  |  | Register Value Lo (20014 | 01 |
|  |  | Register Value Hi (20015) | 0C |
|  |  | Register Value Lo (20015) | 2D |
|  |  | Register Value Hi (20016) | 00 |
|  |  | Register Value Hi (20016 | 00 |
|  |  | Register Value Hi (20017) | FF |
|  |  | Register Value Lo (20017) | FF |
|  |  | Register Value Hi (20018) | FF |
|  |  | Register Value Lo (20018) | FF |
|  |  | Register Value Hi (20019) | FF |
|  |  | Register Value Lo (20019) | FF |
|  |  | Register Value Hi (20020) | FF |
|  |  | Register Value Lo (20020) | FF |
|  |  | Register Value Hi (20021) | FF |
|  |  | Register Value Lo (20021) | FF |
|  |  | Register Value Hi (20022 | FF |
|  |  | Register Value Lo (20022) | FF |
|  |  | Register Value Hi (20023) | FF |
|  |  | Register Value Lo (20023) | FF |
|  |  | Register Value Hi (20024) | FF |
|  |  | Register Value Lo (20024) | FF |
|  |  | Register Value Hi (20025) | FF |
|  |  | Register Value Lo (20025) | FF |
|  |  | Register Value Hi (20026) | FF |
|  |  | Register Value Lo (20026) | FF |
|  |  | Register Value Hi (20027) | FF |
|  |  | Register Value Lo (20027) | FF |
|  |  | Register Value Hi (20028) | FF |
|  |  | Register Value Lo (20028) | FF |
|  |  | Register Value Hi (20029) | FF |
|  |  | Register Value Lo (20029) | FF |
|  |  | Register Value Hi (20030) | FF |
|  |  | Register Value Lo (20030) | FF |
|  |  | Register Value Hi (20031) | FF |
|  |  | Register Value Lo (20031) | FF |
|  |  | Register Value Hi (20032) | FF |
|  |  | Register Value Lo (20032) | FF |
|  |  | Register Value Hi (20033) | FF |
|  |  | Register Value Lo (20033) | FF |
|  |  | Register Value Hi (20034) | FF |
|  |  | Register Value Lo (20034) | FF |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 64. Sample packets for read of schedule day entries.

The response is as follows:

Reg20003–Reg20004  0x0000: 00:00 am, 0x0000: Off time

Reg20005–Reg20006  0x0500: 5:00 am, 0x0001” On time

Reg20007–Reg2008  0x060F: 6:15 am, 0x0000: Off time

Reg20009–Reg20010  0x070F: 7:15 am, 0x0001 – On time

Reg20011–Reg20012  0x0900: 9:00 am, 0x0000: Off time

Reg20013–Reg20014  0x0A1E: 10:30 am, 0x0001: On time

Reg20015–Reg20015  0x0C2D: 12:45 pm, 0x0000: Off time

…

Reg20017–Reg20018  0xFFFF: No entry

…

Multiple Write Changing a Day Schedule

Table 65 is an example of a multiple write to change the Day1 schedule (Function 16, SCH1in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 10 |
| Register Address Hi | 4E | Register Address Hi | 4E |
| Register Address Lo | 23 | Register Address Lo | 23 |
| No. of Registers Hi | 00 | No. of Registers Hi | 00 |
| No. of Registers Lo | 0C | No. of Registers Lo | 0C |
| Register Value Hi (20004) | 06 |  |  |
| Register Value Lo (20004) | 00 |  |  |
| Register Value Hi (20005) | 00 |  |  |
| Register Value Lo (20005) | 01 |  |  |
| Register Value Hi (20006) | 07 |  |  |
| Register Value Lo (20006) | 00 |  |  |
| Register Value Hi (20007) | 00 |  |  |
| Register Value Lo (20007) | 00 |  |  |
| Register Value Hi (20008) | 08 |  |  |
| Register Value Lo (20008) | 00 |  |  |
| Register Value Hi (20009) | 00 |  |  |
| Register Value Lo (20009) | 01 |  |  |
| Register Value Hi (20010) | 12 |  |  |
| Register Value Lo (20010) | 00 |  |  |
| Register Value Hi (20011) | 00 |  |  |
| Register Value Lo (20011) | 00 |  |  |
| Register Value Hi (20012) | 14 |  |  |
| Register Value Lo (20012) | 00 |  |  |
| Register Value Hi (20013) | 00 |  |  |
| Register Value Lo (20013) | 01 |  |  |
| Register Value Hi (20014) | 17 |  |  |
| Register Value Lo (20014) | 2D |  |  |
| Register Value Hi (20015) | 00 |  |  |
| Register Value Lo (20015) | 00 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 65. Sample packets for multiple write changing a day schedule.

Single Write to Remove an Entry

Table 66 is an example of a single write to remove entry 4 (Reg.20008–Reg.20009). Write 0xFFFF to the first entry to remove (Reg.20008).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 06 | Function | 06 |
| Register Address Hi | 4E | Register Address Hi | 4E |
| Register Address Lo | 27 | Register Address Lo | 27 |
| Register Value Hi (20008) | FF | Register Value Hi (20008) | FF |
| Register Value Lo (20008) | FF | Register Value Lo (20008) | FF |
| Register Value Hi (20009) | FF | Register Value Hi (20009) | FF |
| Register Value Lo (20009) | FF | Register Value Lo (20009) | FF |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 66. Sample packets for a single write to remove an entry.

Calendar Objects

Lighting controller contains two calendar objects. A BACNet Calendar object is a list of selected dates. Each date has the format year/month/day/day of week. The first date on the list starts at register address 10004. If the current date in the device object matches an entry in the date list of the Calendar object, then the present value is On; otherwise it is Off. A calendar object can accommodate 90 dates over a 10-year span. Each date entry uses two registers. Table 67 shows the list of calendar and associated registers.

## Calendar (CAL) Object – (Registers 10001 – 10366)

| Register | SCH Object | Type |
| --- | --- | --- |
| 10001 – 10183 | CAL1 | RW |
| 10184 – 10366 | CAL2 | RW |

Table 67. Calendar (CAL) Object Registers

Calendar Object Registers

The calendar object registers are listed in Table  68. Most of the properties can be accessed with Functions 3, 6, and 16. Dates are encoded as follows:

Month = 1–12 (January = 1)

Year = 0–255 (1900–2155)

Register Hi = Year

Register Lo = Month

Day = 1–31

Day of Week = 1–7 (Monday–Sunday)

Register Hi = Day

Register Lo = Day of Week

To add a new entry, read the Date List Count and calculate the next empty slot. For instance, to add Monday May 3, 2004:

The current Date List Count = 3

The next empty slot (Start register of the entry) =
(3 x 2) + 10004

Write to Reg10010–Reg10011 = 0x01030568: Monday May 3, 2004

To delete an entry, write FF to the year, month, day, and day of week. For instance: to delete Monday May 3, 2004:

Write to Reg10010–Reg10011 = 0xFFFFFFFF

Note that due to entry reshuffle after a delete, you can only delete one entry by writing to two registers at a time. You can’t delete an entry and modify another at the same time.

Sample Packets

The following are examples of function requests to calendar object registers.

Read Calendar Properties OutOfService

Table 69 is an example of a read of CAL properties: OutOfService, Value, Date List Count, first and second entries of the date list: Reg10001–Reg10007 (Function 3, CAL 1 in map).

The response is as follows:

Reg10001 (OutOfService) 0x0000: FALSE,

Reg10002 (Value) 0x0000: OFF

Reg10003 (Date List Count) 0x0003: 3 date entries

Reg10004–Reg10005 first entry: 0x050D0268, Friday, Feb 13, 2004

Reg10006–Reg10007 second entry: 0x010F0368, Monday, Mar 15, 2004

| Offset | Modbus Reg. | DB size | Property | Format | Range (Hex) | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 10001 | Bit | OutOfService | On/Off | 0–1 | RW |
| 1 | 10002 | Byte | Value | On/Off | 0–1 | RW |
| 2 | 10003 | Word | Date List Count |  | 0–90 | R |
| Date List |
| 3 | 10004 |  | Day of Week/Day | Int | 0x0101–0xFFFF | RW |
| 4 | 10005 |  | Month/Year | Int | 0x0101–0xFFFF | RW |
| 5 | 10006 –10183 = 89 dates with 2 reg. per date |  | Total of 183 per CAL |  |  |  |

Table 68. Address space for calendar object registers.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 27 | Byte Count | 0E |
| Register Address Lo | 10 | Register Value Hi (10001) | 00 |
| No. of Registers Hi | 10 | Register Value Lo (10001) | 00 |
| No. of Registers Lo | 07 | Register Value Hi (10002) | 00 |
| Packet CRC Hi |  | Register Value Lo (10002) | 00 |
| Packet CRC Lo |  | Register Value Hi (10003) | 00 |
|  |  | Register Value Lo (10003) | 03 |
|  |  | Register Value Hi (10004) | 05 |
|  |  | Register Value Lo (10004) | 0D |
|  |  | Register Value Hi (10005) | 02 |
|  |  | Register Value Lo (10005) | 68 |
|  |  | Register Value Hi (10006) | 01 |
|  |  | Register Value Lo (10006) | 0F |
|  |  | Register Value Hi (10007) | 03 |
|  |  | Register Value Lo (10007) | 68 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 69. Sample packets for a read of CAL properties – OutOfService.

Read Calendar Properties Date List

Table 70 is an example of a read of CAL properties: read the first four entries on the date list: Reg10004–Reg10011 (Function 3, CAL 1in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 27 | Byte Count | 10 |
| Register Address Lo | 10 | Register Value Hi (10004) | 05 |
| No. of Registers Hi | 00 | Register Value Lo (10004) | 0D |
| No. of Registers Lo | 08 | Register Value Hi (10005) | 02 |
| Packet CRC Hi |  | Register Value Lo (10005) | 68 |
| Packet CRC Lo |  | Register Value Hi (10006) | 01 |
|  |  | Register Value Lo (10006) | 0F |
|  |  | Register Value Hi (10007) | 03 |
|  |  | Register Value Lo (10007) | 68 |
|  |  | Register Value Hi (10008) | 04 |
|  |  | Register Value Lo (10085) | 01 |
|  |  | Register Value Hi (10009) | 04 |
|  |  | Register Value Lo (10009) | 68 |
|  |  | Register Value Hi (10010) | FF |
|  |  | Register Value Lo (10010) | FF |
|  |  | Register Value Hi (10011) | FF |
|  |  | Register Value Lo (10011) | FF |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 70. Sample packets for a read of CAL properties – date entries.

The response is as follows:

Reg10004–Reg10005 first entry: 0x050D0268, Friday Feb 13, 2004

Reg10006–Reg10007 second entry: 0x010F0368, Monday Mar 15, 2004

Reg10008–Reg10009 third entry: 0x04010468, Thursday April 1, 2004

Reg10010–Reg10011 fourth entry: 0xFFFFFFFF, empty

Single Write of True to CAL OutOfService

Table 71 is an example of a single write of True to CAL1 OutOfService Reg.10001 (Function 6, CAL 1 in map). The response is that OutOfService is True after the write.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 06 | Function | 06 |
| Register Address Hi | 27 | Register Address Hi | 27 |
| Register Address Lo | 10 | Register Address Lo | 10 |
| Register Value Hi | 00 | Register Value Hi | 00 |
| Register Value Lo | 01 | Register Value Lo | 01 |
| Packet CRC Hi |  | Packet CRC Hi |  |
| Packet CRC Lo |  | Packet CRC Lo |  |

Table 71. Sample packets for a single write of True to CAL1 OutOfService.

Single Write to CAL1 Date List Count

Table72 is an example of a single write of 5 to the CAL1 Date List Count Reg.10003 (Function 6, CAL1 in map). The response is an error code, since the Date List Count is a read-only property.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 06 | Error Code | 86 |
| Register Address Hi | 27 | Exception Code | 85 |
| Register Address Lo | 12 | Packet CRC Hi |  |
| Register Value Hi | 00 | Packet CRC Lo |  |
| Register Value Lo | 05 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 72. Sample packets for a single write to the Date List Count Register.

Multiple Write to Edit Entry in Date List

Table 73 is an example of a multiple write to edit the second entry of the Date List (Function 16, CAL1 in map). This changes the second entry to August 22, 2004: 0x07160868.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 10 | Error Code | 86 |
| Register Address Hi | 27 | Register Address Hi | 27 |
| Register Address Lo | 15 | Register Address Lo | 15 |
| Register Value Hi | 00 | Register Value Hi | 00 |
| Register Value Lo | 02 | Register Value Lo | 05 |
| Reg. Value 1 Hi | 07 | Packet CRC Hi |  |
| Reg. Value 1 Lo | 16 | Packet CRC Lo |  |
| Reg. Value 2 Hi | 08 |  |  |
| Reg. Value 2 Lo | 68 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 73. Sample packets for a multiple write to edit the Date List.

Read Calendar Properties Date List

Table 74 is an example of a read of CAL properties: read the first four entries on the date list after the new entry was added in the previous example: Reg10004–Reg10011 (Function 3, CAL1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 27 | Byte Count | 10 |
| Register Address Lo | 13 | Register Value Hi (10004) | 05 |
| No. of Registers Hi | 00 | Register Value Lo (10004) | 0D |
| No. of Registers Lo | 08 | Register Value Hi (10005) | 02 |
| Packet CRC Hi |  | Register Value Lo (10005) | 68 |
| Packet CRC Lo |  | Register Value Hi (10006) | 07 |
|  |  | Register Value Lo (10006) | 16 |
|  |  | Register Value Hi (10007) | 08 |
|  |  | Register Value Lo (10007) | 68 |
|  |  | Register Value Hi (10008) | 04 |
|  |  | Register Value Lo (10008) | 01 |
|  |  | Register Value Hi (10009) | 04 |
|  |  | Register Value Lo (10009) | 68 |
|  |  | Register Value Hi (10010) | FF |
|  |  | Register Value Lo (10010) | FF |
|  |  | Register Value Hi (10011) | FF |
|  |  | Register Value Lo (10011) | FF |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 74. Sample packets for a read of CAL properties – date entries.

The response is as follows:

Reg10004–Reg10005 first entry: 0x050D0268, Friday Feb 13, 2004                  Reg10006–Reg10007 second entry: 0x07160868, Sunday Aug 22, 2004                                   Reg10008–Reg10009 third entry: 0x04010468, Thursday April 1, 2004

Reg10010–Reg10011 fourth entry: 0xFFFFFFFF, empty

Multiple Write of New Entry to Date List

Table 75 is an example of a multiple write to add a new entry to the date list (Function 16, CAL1 in map).

Note that since we know that CAL has only three entries, to add a new entry, we add the date to the fourth entry: Reg10010–Reg10011. The new entry added is Wednesday May 5, 2004: 0x03050568.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 10 | Function | 10 |
| Register Address Hi | 27 | Register Address Hi | 27 |
| Register Address Lo | 19 | Register Address Lo | 19 |
| Register Value Hi | 00 | Register Value Hi | 00 |
| Register Value Lo | 02 | Register Value Lo | 02 |
| Reg. Value 1 Hi | 03 | Packet CRC Hi |  |
| Reg. Value 1 Lo | 05 | Packet CRC Lo |  |
| Reg. Value 2 Hi | 05 |  |  |
| Reg. Value 2 Lo | 68 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 75. Sample packets for a multiple write of a new entry.Read Calendar Properties Date List

Table 76 is an example of a read of CAL properties: read the first four entries on the date list after the new entry in the previous example: Reg10004–Reg10011 (Function 3, CAL1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 27 | Byte Count | 10 |
| Register Address Lo | 13 | Register Value Hi (10004) | 05 |
| No. of Registers Hi | 00 | Register Value Lo (10004) | 0D |
| No. of Registers Lo | 08 | Register Value Hi (10005) | 02 |
| Packet CRC Hi |  | Register Value Lo (10005) | 68 |
| Packet CRC Lo |  | Register Value Hi (10006) | 07 |
|  |  | Register Value Lo (10006) | 16 |
|  |  | Register Value Hi (10007) | 08 |
|  |  | Register Value Lo (10007) | 68 |
|  |  | Register Value Hi (10008) | 04 |
|  |  | Register Value Lo (10008) | 01 |
|  |  | Register Value Hi (10009) | 04 |
|  |  | Register Value Lo (10009) | 68 |
|  |  | Register Value Hi (10010) | 03 |
|  |  | Register Value Lo (10010) | 05 |
|  |  | Register Value Hi (10011) | 05 |
|  |  | Register Value Lo (10011) | 68 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 76. Sample packets for a read of CAL properties – date entries.

The response is as follows:

Reg10004–Reg10005 first entry: 0x050D0268, Friday Feb 13, 2004

Reg10006–Reg10007 second entry: 0x07160868, Sunday Aug 22, 2004

Reg10008–Reg10009 third entry: 0x04010468, Thursday April 1, 2004

Reg10010–Reg10011 fourth entry: 0x03050568, Wednesday May 5, 2004

Multiple Write to Delete Entry in Date List

Table 77 is an example of a multiple write to delete the second entry in the date list (Function 16, CAL1 in map).

To delete the second entry, set the date to 0xFFFFFFFF. After the deletion, the third and fourth entries are shifted up. Thus the third becomes the second and the fourth becomes the thidd entry. Because of this you can only delete one entry at a time.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 10 | Function | 10 |
| Register Address Hi | 27 | Register Address Hi | 27 |
| Register Address Lo | 15 | Register Address Lo | 15 |
| Register Value Hi | 00 | Register Value Hi | 00 |
| Register Value Lo | 02 | Register Value Lo | 02 |
| Reg. Value 1 Hi | FF | Packet CRC Hi |  |
| Reg. Value 1 Lo | FF | Packet CRC Lo |  |
| Reg. Value 2 Hi | FF |  |  |
| Reg. Value 2 Lo | FF |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 77. Sample packets for a multiple write to delete an entry.

Read Calendar Properties – Date List

Table 78 is an example of a read of CAL properties – read the first four entries on the date list after the entry deletion in the previous example: Reg10004–Reg10011 (Function 3, CAL1 in map).

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 27 | Byte Count | 10 |
| Register Address Lo | 13 | Register Value Hi (10004) | 05 |
| No. of Registers Hi | 00 | Register Value Lo (10004) | 0D |
| No. of Registers Lo | 08 | Register Value Hi (10005) | 02 |
| Packet CRC Hi |  | Register Value Lo (10005) | 68 |
| Packet CRC Lo |  | Register Value Hi (10006) | 04 |
|  |  | Register Value Lo (10006) | 01 |
|  |  | Register Value Hi (10007) | 04 |
|  |  | Register Value Lo (10007) | 68 |
|  |  | Register Value Hi (10008) | 03 |
|  |  | Register Value Lo (10008) | 05 |
|  |  | Register Value Hi (10009) | 05 |
|  |  | Register Value Lo (10009) | 68 |
|  |  | Register Value Hi (10010) | FF |
|  |  | Register Value Lo (10010) | FF |
|  |  | Register Value Hi (10011) | FF |
|  |  | Register Value Lo (10011) | FF |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 78.` Sample packets for a read of CAL properties – date entries.

The response is as follows:

Reg10004–Reg10005 first entry: 0x050D0268, Friday Feb 13, 2004

Reg10006–Reg10007 second entry: 0x04010468, Thursday April 1, 2004

Reg10008–Reg10009 third entry: 0x03050568, Wednesday May 5, 2004

Reg10010–Reg10011 fourth entry: 0xFFFFFFFF, Empty

Compact Event Log

The Lighting Controller uses an object known as the compact event log to store system events. This is a first-in, first-out rotary buffer with a depth adjustable to a maximum of 1500 events. Each event has eight components that can be reported. If the buffer overflows, the oldest event is discarded to make room for the latest. A register is available that contains the number of events in the log. If the log is empty and an attempt is made to read out an event, an exception is returned. Events are read using Function Code 04.

Event Definitions

Table 80 lists the types of events that can be present in the compact event log. Asking for more events than are present in the event log causes an exception. Read register 20001 and 20002 to get the number of events and ask for 12n registers to get the nth number of entries.

| Offset | Modbus reg. | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 20001- 20002 | Byte | Total Events | Int | 1 – 1500 | R |
|  |  |  | Alarm Output Ref. |  |  |  |
| 2 | 20003 | Word | Device No | Word | 0 - 65535 | R |
| 3 | 20004 | Word | Object Type | Word | 0 – 65535 | R |
| 4 | 20005 | Word | Object Instance | Word | 0 – 65535 BO= 4 BV= 5 | R |
| 5 | 20006 | Byte | Alarm Ack | Int | 0/1 | R |
| 6 | 20007- 20008 | Byte | Alarm Values | Int | 0 - 65535, 0 - 65535 | R |
|  |  | Array of 1500 | Event Entries |  |  |  |
| 8 | 20009 |  | Hrs/Mins | Int | 0 – 23 ¦ 0 - 59 | R |
| 9 | 20010 |  | Seconds/Hundredths of sec | Int | 0 – 59 ¦ 0 - 99 | R |
| 10 | 20011 |  | Week of Day / Day | Int | 0 – 07 ¦ 0 – 31 | R |
| 11 | 20012 |  | Month / Year | Int | 0 – 12 ¦ 0 – 99 | R |
| 12 | 20013 |  | Event Type | Int | Enum | R |
| 13 | 20014 |  | Event Argument | Int | Enum | R |
|  |  |  | Event Object Ref. |  |  |  |
| 14 | 20015 |  | Object Type | WORD | 0 – 65535 | R |
| 15 | 20016 |  | Object Instance | WORD | 0 – 65535 | R |
| 16 –12007 | 20017 – 32008 |  | 1499 more Event entries (8 registers per entry) |  |  |  |
|  |  |  | 12007 registers per CEL |  |  |  |

Table 79. Registers comprising the compact event log.

Each event record is a block of eight registers starting from 20009. Note that these registers are read only. The Alarm Output Ref and Alarm Ack properties are editable. Note that if Alarm Output Reference does not exist, all three registers are filled with 0xFFFF.

Compact Event Log Registers

The registers of the compact event log are listed in Table 79.

| Event Type | Number |  | Event Type | Number |
| --- | --- | --- | --- | --- |
| NONE | 0 |  | OVER VOLT | 80 |
| TIME CHG | 58 |  | ALARM | 81 |
| DEV ONLINE | 59 |  | ALARM ACK | 82 |
| DEV OFFLINE | 60 |  | BRKR TRIP | 83 |
| DEV RESET | 61 |  | BRKR TRIP RESTORED | 84 |
| DB LOAD | 66 |  | PHASE ERR RESTORED | 85 |
| DB SAVE | 67 |  | OVER VOLT RESTORED | 86 |
| DB CLEAR | 68 |  | UNDER VOLT RESTORED | 87 |
| DEAD BATT | 74 |  | DEAD BATT RESTORED | 88 |
| PHASE ERR | 75 |  | CMD FAIL RESTORED | 89 |
| CMD FAIL | 76 |  | BRKR SHORTED | 90 |
| STATUS ON | 77 |  | BRKR SHORT RESTORED | 91 |
| STATUS OFF | 78 |  | OTHER EVENT | 92 |
| UNDER VOLT | 79 |  |  |  |

Table 80. Event definitions

** Asking for more events than exist will cause an exception.  Read register 20001 and 20002 to get number of events and ask for n * 12 registers to get nth number of entries.

Sample Packets

Following are examples of function requests to the compact event log.

Ask for Compact Event Log Event #1

Table 81 is an example of a request for Event#1 Reg20007–Reg20014 (Function 4, CEL1 in map).

The response is as follows:

Reg20007–Reg20008 Time: 16:37:27.60

Reg20009–Reg20010 Date: Wed May 26, 2004

Reg200011 Event Type: 0x003D, Device Reset

Reg20012 Event Argument: 0x0000

Reg20013–Reg20014 Event Object Ref: 0x00090064, DEV100

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 4E | Byte Count | 10 |
| Register Address Lo | 26 | Register Value Hi (20007) | 10 |
| Registers Hi | 00 | Register Value Lo (20007) | 25 |
| Registers Lo | 08 | Register Value Hi (20008) | 1B |
| Packet CRC Hi |  | Register Value Lo (20008) | 3C |
| Packet CRC Lo |  | Register Value Hi (20009) | 03 |
|  |  | Register Value Lo (20009) | 1A |
|  |  | Register Value Hi (20010) | 05 |
|  |  | Register Value Lo (20010) | 68 |
|  |  | Register Value Hi (20011) | 00 |
|  |  | Register Value Lo (20011) | 3D |
|  |  | Register Value Hi (20012) | 00 |
|  |  | Register Value Lo (20012) | 00 |
|  |  | Register Value Hi (20013) | 00 |
|  |  | Register Value Lo (20013) | 09 |
|  |  | Register Value Hi (20014) | 00 |
|  |  | Register Value Lo (20014) | 64 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 81. Sample packets for request for compact event log event #1.

Ask for Compact Event Log Total Events

Table 82 is an example of a request for Compact Event Log Total Events, Alarm Output Ref Reg20001–Reg20005.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Function | 04 |
| Register Address Hi | 4E | Byte Count | 06 |
| Register Address Lo | 20 | Register Value Hi (20001) | 00 |
| Registers Hi | 00 | Register Value Lo (20001) | 00 |
| Registers Lo | 05 | Register Value Hi (20002) | 00 |
| Packet CRC Hi |  | Register Value Lo (20002) | 12 |
| Packet CRC Lo |  | Register Value Hi (20003) | 00 |
|  |  | Register Value Lo (20003) | 64 |
|  |  | Register Value Hi (20004) | 00 |
|  |  | Register Value Lo (20004) | 05 |
|  |  | Register Value Hi (20005) | 00 |
|  |  | Register Value Lo (20005) | 44 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table 82. Sample packets for request for compact event log total events.

The response is as follows:

Reg20001–Reg 20002 Total Event: 0x00000012, 18 decimal

Reg20003–Reg20005 Alarm Output: Ref. 0x006400050044, 100.BO68 (Alarm Relay)

Ask for Compact Event Log Nonexistent Event

Table 83 is an example of a request for Event #21, Reg20173–Reg20180, which does not exist. The response is an error return for invalid data value, since there are only 18 events in the list.

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 04 | Error Code | 84 |
| Register Address Hi | 4E | Exception Code | 03 |
| Register Address Lo | CC | Packet CRC Hi |  |
| Registers Hi | 00 | Packet CRC Lo |  |
| Registers Lo | 08 |  |  |
| Packet CRC Hi |  |  |  |
| Packet CRC Lo |  |  |  |

Table 83. Sample packets for request for nonexistent event.

## Compact Event Log (CEL) – Setup (Registers 60001 – 60008)

Table 84 shows the registers to set up  alarm events and alarm output reference.

|  | Modbus reg. | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 60001- 60002 | Byte | Total Events | Int | 1 – 2000 | R |
|  |  |  | Alarm Output Ref. |  |  |  |
| 2 | 60003 | Word | Device No | Word | 0 - 65535 | R |
| 3 | 60004 | Word | Object Type | Word | 0 – 65535 BO= 4 BV= 5 | R |
| 4 | 60005 | Word | Object Instance | Word | 0 – 65535 | R |
| 5 | 60006 | Byte | Alarm Ack | Int | 0/1 | R/W |
| 6 | 60007- 60008 | Byte | Alarm Values | Int | 0 - 65535, 0 - 65535 | R/W |

Table 84. registers to set up  alarm events and alarm output reference

*Note: Registers 60001 to 60005 must not be written to even though the can be viewed with Function 3.

| Alarm Values Enabled | Reg 60007 (Hexadecimal) | Reg 60008 (Hexadecimal) |
| --- | --- | --- |
| None | 0000 | 0000 |
| Lighting Alarms, | 0000 | 0800 |
| Lighting Statuses, | 1000 | 0000 |
| Lighting Alarms, Lighting Statuses, | 1000 | 0800 |
| Time Change | 0002 | 0000 |
| Time Change, Lighting Alarms | 0002 | 0800 |
| Time Change, Lighting Statuses, | 1002 | 0000 |
| Time Change, Lighting Alarms, Lighting Statuses | 1002 | 0800 |
| Device Statuses, | 2000 | 0000 |
| Device Statuses, Lighting Alarms, | 2000 | 0800 |
| Device Statuses, Lighting Statuses, | 3000 | 0000 |
| Device Statuses, Lighting Alarms, Lighting Statuses, | 3000 | 0800 |
| Device Statuses, Time Change | 2002 | 0000 |
| Device Statuses, Time Change, Lighting Alarms | 2002 | 0800 |
| Device Statuses, Time Change, Lighting Statuses, | 0800 | 0000 |
| Device Statuses, Time Change, Lighting Alarms, Lighting Statuses | 3002 | 0800 |

Table 85. possible register values for every Lighting Alarm Value combination

Alarm Acknowledge:  Register 60006 will always display 0000 hex.  If the Alarm Relay is active writing 0001 hex will acknowledge the Alarm. *When alarm is acknowledged the value of the register will go back to 0000hex.

Alarm Values: Register 60007 – 60008 display the value of the CEL Alarm Values bit list.   Table 85 displays all

possible register values for every Lighting Alarm Value combination possible in the Compact Event Log.

Load Shedding

The Load Shed object defines the Outputs that will be turned Off, in response to a request for the controller to reduce its the electrical load.  Each output can be assigned to one of 5 Shed Levels (Table 87) (to define its priority is relation to the Load Shed request). The lower the priority, the more likely the output is to be turned Off (0 prevents the output from being shed).  The Load Shed object properties are read by Function Codes 3/6/16 and written to using Function Codes 6/16. Table 86 lists Load Shed Registers.

Load Shed (LS) object – (Registers 30001 – 30069)

| Offset | Modbus Regs | DB size | Property | Format | Range | Type |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 30001 | BYTE | Value | WORD | 0 – 3 | R |
| 1 | 30002 | WORD | Shed Duration | WORD | 0 – 65535 | RW |
| 2 | 30003 | BYTE | Shed Level | WORD | 0 -5 | RW |
|  |  |  | Controlled Object Shed Level |  |  |  |
| 3 | 30004 | BYTE | BO1 – Shed Level | WORD | 0-5 | RW |
| 4 | 30005 | BYTE | BO1 – Shed Level | WORD | 0-5 | RW |
|  | … |  | … |  |  |  |
| 68 | 30069 | BYTE | BO66 – Shed Level | WORD | 0-5 | RW |

Table 86. Load shed registers.

| Type | Number | Comments |
| --- | --- | --- |
| Level 0 | 0 | No Shedding Required |
| Level 1 | 1 |  |
| Level 2 | 2 |  |
| Level 3 | 3 |  |
| Level 4 | 4 |  |
| Level 5 | 5 |  |

Table 87. Shed Level definitions

Sample Packets

| Request | Response |
| --- | --- |
| Field Name | Hex | Field Name | Hex |
| Device Address | 01 | Device Address | 01 |
| Function | 03 | Function | 03 |
| Register Address Hi | 75 | Byte Count | 06 |
| Register Address Lo | 30 | Register Value Hi (30001) | 00 |
| Registers Hi | 00 | Register Value Lo (30001) | 00 |
| Registers Lo | 03 | Register Value Hi (30002) | 00 |
| Packet CRC Hi |  | Register Value Lo (30002) | 05 |
| Packet CRC Lo |  | Register Value Hi (30003) | 00 |
|  |  | Register Value Lo (30003) | 02 |
|  |  | Packet CRC Hi |  |
|  |  | Packet CRC Lo |  |

Table88. Simple packets for read of all LS1 properties.

Table 88 is an example of reading all the LS1 properties: Value, Shed Duration, and Shed Level.

The response is as follows:

Reg30001 (Value): 0x0000, Inactive,

Reg30002 (Shed Duration): 0x0005, 5 minutes

Reg30003 (Shed Level): 0x0002, Shed Extraneous

Summary of Registers

Table 89 is a summarized list of all the lighting controller registers.

| System Variable | Delta Object | Instance Range | Property(s) | Value range | Func. 1/5/15 | Func. 2 | Func. 3/6/16 | Func. 4 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Device registers | Device | 1 | Various | Various |  |  |  | 10001 – 10046 |
| Device Setup | Device | 1 | Various | Various |  |  | 50001 – 50046 |  |
| Physical Inputs | Multi-state Input (SW) | 101 – 116 | Value | Enumerated |  |  |  | 1 – 16 |
| Physical Inputs | Multi-state Input (SW) | 201 – 216 | Value | Enumerated |  |  |  | 17 – 32 |
| Physical Inputs | Multi-state Input (SW) | 301 – 316 | Value | Enumerated |  |  |  | 33 – 48 |
| Physical Inputs | Multi-state Input (SW) | 401 – 416 | Value | Enumerated |  |  |  | 49 – 64 |
| Physical Inputs | Multi-state Input (SW) | 501 – 516 | Value | Enumerated |  |  |  | 65 – 80 |
| Multi-State Input Setup | Multi-state Input (SW) | 101 – 116 | Setup | Various |  |  | 40001 – 40148 |  |
| Multi-State Input Setup | Multi-state Input (SW) | 201 – 216 | Setup | Various |  |  | 40101 – 40148 |  |
| Multi-State Input Setup | Multi-state Input (SW) | 301 – 316 | Setup | Various |  |  | 40201 – 40248 |  |
| Multi-State Input Setup | Multi-state Input (SW) | 401 – 416 | Setup | Various |  |  | 40301 – 40348 |  |
| Multi-State Input Setup | Multi-state Input (SW) | 501 – 516 | Setup | Various |  |  | 40401 – 40448 |  |
| Physical Inputs | Analog Input | 1 – 3 | Value | Float |  |  |  | 101 – 106 |
| Physical Inputs | Analog Input | 601 – 608 | Value | Float |  |  |  | 117 – 132 |
| Physical Inputs | Analog Input | 701 – 708 | Value | Float |  |  |  | 133 – 148 |
| Physical Inputs | Analog Input | 1 – 3 | Various | Various |  |  | 1001 – 1027 |  |
| Physical Inputs | Analog Input | 601 – 608 | Various | Various |  |  | 1101 – 1172 |  |
| Physical Inputs | Analog Input | 701 – 708 | Various | Various |  |  | 1201 – 1272 |  |
| Physical Input Setup | Analog Variable | 601 – 608 | Value | Float |  |  | 1301 – 1364 |  |
| Physical Input Setup | Analog Variable | 701 – 708 | Value | Float |  |  | 1401 – 1464 |  |
| System Variable | Delta Object | Instance Range | Property(s) | Value range | Func. 1/5/15 | Func. 2 | Func. 3/6/16 | Func. 4 |
| Physical Outputs | Binary Output | 1 to 66 | Value | On/Off | 1 – 66 |  |  |  |
| Outputs Feedback | Binary Output | 1 to 66 | Feedback Value | On/Off |  | 1-66 |  |  |
| Physical Outputs | Binary Output | 1 - 70 | OutOfService | On/Off | 201 – 270 |  |  |  |
| Special Outputs | Binary Output | 67 – 70 | Value | On/Off | 67 – 70 |  |  |  |
| Physical Outputs | Binary Output | 1 - 70 | Various | Various |  |  | 2001 – 3260 |  |
| Physical Output Override | Binary Variable | 1 to 66 | Override Value | On/Off |  |  | 3401 – 3466 |  |
| System Variable | Delta Object | Instance Range | Property(s) | Value range | Func. 1/5/15 | Func. 2 | Func. 3/6/16 | Func. 4 |
| Lighting Group | Lighting Group | 1 to 16 | Value | On/Off | 301 – 316 |  |  |  |
| Lighting Group | Lighting Group | 1 to 16 | OutOfService | On/Off | 401 - 416 |  |  |  |
| Lighting Group Setup | Lighting Group | 1 to 16 | Setup | Various |  |  | 4001 – 9808 |  |
| Schedule | Schedule | 1 to 16 | Value | On/Off | 501 - 516 |  |  |  |
| Schedule | Schedule | 1 to 16 | OutOfService | On/Off | 601 - 616 |  |  |  |
| Schedule | Schedule | 1 to 16 | Setup | Various |  |  | 20001 – 24640 |  |
| Calendar | Calendar | 1 | Setup | Various |  |  | 10001 – 10366 |  |
| Events | Compact Event Log | 1 | Event records | Record |  |  |  | 20001 to 32008 |
| Events Log Setup | Compact Event Log | 1 | Event records | Record |  |  | 60001 – 60008 |  |
| Load Shed | Load Shed | 1 | Various | Various |  |  | 30001 – 30069 |  |

Table 89.Summary of Registers

g

GE Consumer & Industrial

General Electric Company

41 Woodford Ave., Plainville, CT 06062

DEH41097  R02  1004	© 2004 General Electric Company