## Activating Modbus on the Meter
Activating Modbus in the Meter
1. Verify if the meter is in Hunt mode by looking at Serial # Registers in the LCD screen of the meter.
2. Using HyperTerminal Private Edition, go to View->Key Macros. Establish a new function key to login into the meter. The login syntax is “attn –S7000#### -5lEvElbAl”, where 7000#### is the serial number of the meter.
Note: You may download HTPE at this site http://www.hilgraeve.com/htpe/download.html
3. Press the connect button in your HyperTerminal session. Start pressing the function key that will log you in the meter. Since the meter is on Hunt mode, it will scan through the 9600, 19200, and 38400 baud rates. Once it gets to 19200, you will be able
4. Once logged in, change the poll address (modbus ID number) of the meter to the desired poll address by typing in “attn –p###<enter>” in the CIP# prompt, where ### is the desired poll number. Save the change by typing in “attn –W1234<enter>”. Type in “a
5. Change the baudrate of the meter to 19200 by typing “stty 19200<enter 2x>” at the CIP# prompt. To activate modbus type in “stty –M1<enter 2x>”. Save the changes by typing “stty –W1234<enter 2x>”. To check if the meter is set to 19200, type in “stty” an
6. Type in “halt” at the CIP# prompt. This should restart the meter with the new setting.
7. To turn off Modbus, login in to the meter and then type “stty –M0”. Save settings by typing “stty –W1234”.
8. Exit out of the meter by typing attn or exit.
9. Follow the same procedures for the other meters.

## RSM5 Modbus Memory Map
| ADDRESS (HEX) | ADDRESS (DEC) | ADDRESS (HEX) | ADDRESS (XXXX) | REGISTER DATA TYPE | (R)EAD OR (W)RITE | REGISTER LABEL | REGISTER DESCRIPTION | REGISTER UNITS | NOTES
R4XXXX | 0 | 0 | 1 | 1 | 32-BIT LONG INTEGER | R | SERNO_REG | METER SERIAL NO. | HEX
R4XXXX | 2 | 2 | 3 | 3 | 16-BIT INTEGER | R | SERNO_EXTENSION_REG | METER SERIAL NO. EXTENSION | HEX | RETURNS SAME VALUE AS ADDRESS 0000
R4XXXX | 4 | 4 | 5 | 5 | 32-BIT LONG INTEGER | R | VERSION_REG | METER VERSION NUMBER | HEX
R4XXXX | 6 | 6 | 7 | 7 | 16-BIT INTEGER | R | VERSION_EXTENSION_RE | METER VERSION NUMBER EXTENSION | HEX | RETURNS SAME VALUE AS ADDRESS 0000
R4XXXX | 8 | 8 | 9 | 9 | 16-BIT INTEGER | R | MODBUS_ADDR_REG | METER MODBUS ADDRESS |  | 8-BIT MODBUS ADDRESS IN LSB
R4XXXX | 9 | 9 | A | 10 | 16-BIT INTEGER | R | BAUDRATE_REG | BAUD RATE
R4XXXX | C | 12 | D | 13 | 16-BIT INTEGER | R | METER_STATUS_REG | METER STATUS |  | ALWAYS 1 FOR MODBUS
R4XXXX | D | 13 | E | 14 | 16-BIT INTEGER | R | METER_READY_REG | METER READY |  | ALWAYS 1 FOR MODBUS
R4XXXX | E | 14 | F | 15 | 16-BIT INTEGER | R | NUM_METERS_REG | NUMBER 0F METERS CONFIGURED |  | ALWAYS 1 FOR RSM-5
R4XXXX | F | 15 | 10 | 16 | 16-BIT INTEGER | R | NUM_REALTIME_MTRS_RE | NUMBER OF REAL-TIME POINTS CONFIGURED
R4XXXX | 10 | 16 | 11 | 17 | 16-BIT INTEGER | R | NUM_INTERVAL_MTRS_RE | NUMBER OF INTERVAL POINTS CONFIGURED |  | RETURNS 0 IF INTERVALS ARE DISABLED
R4XXXX | 11 | 17 | 12 | 18 | 16-BIT INTEGER | R | NUM_MAX_MIN_MTRS_REG | NUMBER OF MAX/MIN POINTS CONFIGURED |  | ALWAYS RETURNS 0
R4XXXX | 12 | 18 | 13 | 19 | 16-BIT INTEGER | R | MAX_INTERVALS_RECORD | MAXIMUM NUMBER OF INTERVALS THAT CAN RECORDED |  | DEPENDENT UPON THE NUMBER OF PARAMETERS OPTIONED AND THE NUMBER OF METERS RETURNED IN ADDRESS 0015
R4XXXX | 31 | 49 | 32 | 50 | 16-BIT INTEGER | R | READ_INTERVAL_LENGTH | STORED INTERNAL LENGTH | MINUTES | INTERVAL LENGTH IN MINUTES MUST BE EVENLY DIVISIBLE INTO 60 (1, 2, 3, 4, 5, 6, 10, 12, 15, 20, 30, 60)
R4XXXX | 32 | 50 | 33 | 51 | 16-BIT INTEGER | R | READ_TIME_REG | INTERNAL TIME - HOURS/MINUTES | HOURS/MINUTES | HOURS: 0-23 (BITMASK=FF00); MINUTES: 0-59 (BITMASK = 00FF)
R4XXXX | 33 | 51 | 34 | 52 | 16-BIT INTEGER | R | READ_SECONDS_REG | INTERNAL TIME - SECONDS | SECONDS
R4XXXX | 34 | 52 | 35 | 53 | 16-BIT INTEGER | R | READ_DATE_REG | INTERNAL DATE - MONTH/DAY | MONTH/DAY
R4XXXX | 35 | 53 | 36 | 54 | 16-BIT INTEGER | R | READ_YEAR_REG | INTERNAL DATE - YEAR | YEAR
R4XXXX | 36 | 54 | 37 | 55 | 16-BIT INTEGER | W | SET_TIME_REG | INTERNAL TIME - HOURS/MINUTES | HOURS/MINUTES | HOURS: 0-23 (BITMASK=FF00); MINUTES: 0-59 (BITMASK = 00FF)
R4XXXX | 37 | 55 | 38 | 56 | 16-BIT INTEGER | W | SET_SECONDS_REG | INTERNAL TIME - SECONDS | SECONDS
R4XXXX | 38 | 56 | 39 | 57 | 16-BIT UNSIGNED INTEGER | W | SET_DATE_REG | INTERNAL DATE - MONTH/DAY | MONTH/DAY
R4XXXX | 39 | 57 | 3A | 58 | 16-BIT UNSIGNED INTEGER | W | SET_YEAR_REG | INTERNAL DATE - YEAR | YEAR | YYYY
R4XXXX | 3A | 58 | 3B | 59 | 16-BIT INTEGER | R | OLDEST_INTERVAL_TIME | DATE/TIME OF OLDEST INTERVAL - HOURS/MINUTES | HOURS/MINUTES | HOURS: 0-23 (BITMASK=FF00); MINUTES: 0-59 (BITMASK = 00FF); DDE DATA IS COM COMPATIBLE, DATE/TIME NUMERIC
R4XXXX | 3B | 59 | 3C | 60 | 16-BIT INTEGER | R | OLDEST_INTERVAL_DATE | DATE/TIME OF OLDEST INTERVAL - MONTH/DAY | MONTH/DAY | MONTH: 1=JAN, 12=DEC (BITMASK=FF00); DAY: 1-31 (BITMASK=00FF); DDE DATA IS COM COMPATIBLE, DATE/TIME NUMERIC
R4XXXX | 3C | 60 | 3D | 61 | 16-BIT UNSIGNED INTEGER | R | OLDEST_INTERVAL_YEAR | DATE/TIME OF OLDEST INTERVAL - YEAR | YEAR | YYYY
R4XXXX | 3D | 61 | 3E | 62 | 16-BIT INTEGER | R | NEWEST_INTERVAL_TIME | DATE/TIME OF NEWEST INTERVAL - HOURS/MINUTES | HOURS/MINUTES | HOURS: 0-23 (BITMASK=FF00); MINUTES: 0-59 (BITMASK = 00FF); DDE DATA IS COM COMPATIBLE, DATE/TIME NUMERIC
R4XXXX | 3E | 62 | 3F | 63 | 16-BIT INTEGER | R | NEWEST_INTERVAL_DATE | DATE/TIME OF NEWEST INTERVAL - MONTH/DAY | MONTH/DAY | MONTH: 1=JAN, 12=DEC (BITMASK=FF00); DAY: 1-31 (BITMASK=00FF); DDE DATA IS COM COMPATIBLE, DATE/TIME NUMERIC
R4XXXX | 3F | 63 | 40 | 64 | 16-BIT UNSIGNED INTEGER | R | NEWEST_INTERVAL_YEAR | DATE/TIME OF NEWEST INTERVAL - YEAR | YEAR | YYYY
R4XXXX | 40 | 64 | 41 | 65 | 16-BIT INTEGER | R/W | SELECT_INTERVAL_TIME | DATE/TIME OF CURRENTLY SELECTED INTERVAL - HOURS/MINUTES | HOURS/MINUTES | HOURS: 0-23 (BITMASK=FF00); MINUTES: 0-59 (BITMASK = 00FF); DDE DATA IS COM COMPATIBLE, DATE/TIME NUMERIC
R4XXXX | 41 | 65 | 42 | 66 | 16-BIT INTEGER | R/W | SELECT_INTERVAL_DATE | DATE/TIME OF CURRENTLY SELECTED INTERVAL - MONTH/DAY | MONTH/DAY | MONTH: 1=JAN, 12=DEC (BITMASK=FF00); DAY: 1-31 (BITMASK=00FF); DDE DATA IS COM COMPATIBLE, DATE/TIME NUMERIC
R4XXXX | 42 | 66 | 43 | 67 | 16-BIT UNSIGNED INTEGER | R/W | SELECT_INTERVAL_YEAR | DATE/TIME OF CURRENTLY SELECTED INTERVAL - YEAR | YEAR | YYYY
R4XXXX | 43 | 67 | 44 | 68 | 16-BIT INTEGER | R/W | DATE_TIME_CURRENT_IN | DATA READY FLAG |  | MASK OUT/IGNORE BIT 15; 0=DATA IS READY FOR READ; 1=POPULATE REGISTERS WITH TIMESTAMPT DATA; 2=INVALID TIMESTAMP REQUESTED; STORED DYNAMIC DATA READY FOR READ
R4XXXX | 63 | 99 | 64 | 100 | 16-BIT UNSIGNED INTEGER | R | INTERVAL_DATA_QUALIF | INTERVAL DATA QUALIFYING REGISTER |  | 8=INVALID INTERVAL
R4XXXX | 64 | 100 | 65 | 101 | 32-BIT FLOATING POINT | R | 3PHASE_KW | THREE-PHASE TOTAL KW | KW | STORED INTERVAL 1 FOR METER #1
R4XXXX | 66 | 102 | 67 | 103 | 32-BIT FLOATING POINT | R | 3PHASE_KVAR | THREE-PHASE TOTAL KVAR | KVAR | STORED INTERVAL 2 FOR METER #1
R4XXXX | 68 | 104 | 69 | 105 | 32-BIT FLOATING POINT | R | 3PHASE_KVA | THREE-PHASE TOTAL KVA | KVA | STORED INTERVAL 3 FOR METER #1
R4XXXX | 6A | 106 | 6B | 107 | 32-BIT FLOATING POINT | R | 3PHASE_PF | THREE-PHASE TOTAL POWER FACTOR |  | STORED INTERVAL 4 FOR METER #1
R4XXXX | 162 | 354 | 163 | 355 | 32-BIT FLOATING POINT | R | LINE_FREQ_REG | FREQUENCY (PHASE A) | HZ | PHASE-TO-NEUTRAL INSTANTANEOUS FREQUENCY
R4XXXX | 16A | 362 | 16B | 363 | 32-BIT FLOATING POINT | R | V_A_REG | VOLTAGE (A-N) | V | PHASE-TO-NEUTRAL INSTANTANEOUS VOLTAGE
R4XXXX | 16C | 364 | 16D | 365 | 32-BIT FLOATING POINT | R | V_B_REG | VOLTAGE (B-N) | V | PHASE-TO-NEUTRAL INSTANTANEOUS VOLTAGE
R4XXXX | 16E | 366 | 16F | 367 | 32-BIT FLOATING POINT | R | V_C_REG | VOTLAGE (C-N) | V | PHASE-TO-NEUTRAL INSTANTANEOUS VOLTAGE
R4XXXX | 170 | 368 | 171 | 369 | 32-BIT FLOATING POINT | R | VOLT_A_REG | VOLTAGE - CT01 | V | CT01 INSTANTANEOUS VOLTAGE
R4XXXX | 172 | 370 | 173 | 371 | 32-BIT FLOATING POINT | R | AMP_A_REG | CURRENT - CT01 | A | CT01 INSTANTANEOUS CURRENT
R4XXXX | 174 | 372 | 175 | 373 | 32-BIT FLOATING POINT | R | KW_A_REG | REAL POWER - CT01 | KW | CT01 INSTANTANEOUS REAL POWER
R4XXXX | 176 | 374 | 177 | 375 | 32-BIT FLOATING POINT | R | KVAR_A_REG | REACTIVE POWER - CT01 | KAVR | CT01 INSTANTANEOUS REACTIVE POWER
R4XXXX | 178 | 376 | 179 | 377 | 32-BIT FLOATING POINT | R | KVA_A_REG | APPARENT POWER - CT01 | KVAR | CT01 INSTANTANEOUS APPARENT POWER
R4XXXX | 17A | 378 | 17B | 379 | 32-BIT FLOATING POINT | R | VOLT_B_REG | VOLTAGE - CT02 | V | CT02 INSTANTANEOUS VOLTAGE
R4XXXX | 17C | 380 | 17D | 381 | 32-BIT FLOATING POINT | R | AMP_B_REG | CURRENT - CT02 | A | CT02 INSTANTANEOUS CURRENT
R4XXXX | 17E | 382 | 17F | 383 | 32-BIT FLOATING POINT | R | KW_B_REG | REAL POWER - CT02 | KW | CT02 INSTANTANEOUS REAL POWER
R4XXXX | 180 | 384 | 181 | 385 | 32-BIT FLOATING POINT | R | KVAR_B_REG | REACTIVE POWER - CT02 | KAVR | CT02 INSTANTANEOUS REACTIVE POWER
R4XXXX | 182 | 386 | 183 | 387 | 32-BIT FLOATING POINT | R | KVA_B_REG | APPARENT POWER - CT02 | KVAR | CT02 INSTANTANEOUS APPARENT POWER
R4XXXX | 184 | 388 | 185 | 389 | 32-BIT FLOATING POINT | R | VOLT_C_REG | VOLTAGE - CT03 | V | CT03 INSTANTANEOUS VOLTAGE
R4XXXX | 186 | 390 | 187 | 391 | 32-BIT FLOATING POINT | R | AMP_C_REG | CURRENT - CT03 | A | CT03 INSTANTANEOUS CURRENT
R4XXXX | 188 | 392 | 189 | 393 | 32-BIT FLOATING POINT | R | KW_C_REG | REAL POWER - CT03 | KW | CT03 INSTANTANEOUS REAL POWER
R4XXXX | 18A | 394 | 18B | 395 | 32-BIT FLOATING POINT | R | KVAR_C_REG | REACTIVE POWER - CT03 | KAVR | CT03 INSTANTANEOUS REACTIVE POWER
R4XXXX | 18C | 396 | 18D | 397 | 32-BIT FLOATING POINT | R | KVA_C_REG | APPARENT POWER - CT03 | KVAR | CT03 INSTANTANEOUS APPARENT POWER
R4XXXX | 288 | 648 | 289 | 649 | 32-BIT FLOATING POINT | R | 3_PHASE_KWH | THREE-PHASE KWH | KWH | METER #1 REAL TIME INPUT 1
R4XXXX | 28A | 650 | 28B | 651 | 32-BIT FLOATING POINT | R | 3_PHASE_KVARH | THREE-PHASE KVARH | KVARH | METER #1 REAL TIME INPUT 2
R4XXXX | 28C | 652 | 28D | 653 | 32-BIT FLOATING POINT | R | 3_PHASE_KW | THREE-PHASE KW | KW | METER #1 REAL TIME INPUT 3
R4XXXX | 28E | 654 | 28F | 655 | 32-BIT FLOATING POINT | R | 3_PHASE_KVAR | THREE-PHASE KVAR | KVAR | METER #1 REAL TIME INPUT 4
R4XXXX | 290 | 656 | 291 | 657 | 32-BIT FLOATING POINT | R | 3_PHASE_KVA | THREE-PHASE KVA | KVA | METER #1 REAL TIME INPUT 5
R4XXXX | 292 | 658 | 293 | 659 | 32-BIT FLOATING POINT | R | 3_PHASE_PF | THREE-PHASE POWER FACTOR |  | METER #1 REAL TIME INPUT 6
R4XXXX | 3E8 | 1000 | 3E9 | 1001 | 32-BIT FLOATING POINT | R | THD_A | THD PHASE A | % | METER #1 TOTAL HARMONIC DISTORTION
R4XXXX | 3EA | 1002 | 3EB | 1003 | 32-BIT FLOATING POINT | R | PHASE_ANGLE_A | PHASE ANGLE A | DEGREES | METER #1 PHASE ANGLE
R4XXXX | 3EC | 1004 | 3ED | 1005 | 32-BIT FLOATING POINT | R | VOLTS_PH_TO_PH_A | PHASE-TO-PHASE VOLTAGE A | V | METER #1 INSTANTANEOUS VOLTAGE
R4XXXX | 3EE | 1006 | 3EF | 1007 | 32-BIT FLOATING POINT | R | THD_B | THD PHASE B | % | METER #1 TOTAL HARMONIC DISTORTION
R4XXXX | 3F0 | 1008 | 3F1 | 1009 | 32-BIT FLOATING POINT | R | PHASE_ANGLE_B | PHASE ANGLE B | DEGREES | METER #1 PHASE ANGLE
R4XXXX | 3F2 | 1010 | 3F3 | 1011 | 32-BIT FLOATING POINT | R | VOLTS_PH_TO_PH_B | PHASE-TO-PHASE VOLTAGE B | V | METER #1 INSTANTANEOUS VOLTAGE
R4XXXX | 3F4 | 1012 | 3F5 | 1013 | 32-BIT FLOATING POINT | R | THD_C | THD PHASE C | % | METER #1 TOTAL HARMONIC DISTORTION
R4XXXX | 3F6 | 1014 | 3F7 | 1015 | 32-BIT FLOATING POINT | R | PHASE_ANGLE_C | PHASE ANGLE C | DEGREES | METER #1 PHASE ANGLE
R4XXXX | 3F8 | 1016 | 3F9 | 1017 | 32-BIT FLOATING POINT | R | VOLTS_PH_TO_PH_C | PHASE-TO-PHASE VOLTAGE C | V | METER #1 INSTANTANEOUS VOLTAGE
R4XXXX | 7D0 | 2000 | 7D1 | 2001 | 16-BIT INTEGER | R | NUMPH_OFFSET | NUMBER OF PHASES |  | 1, 2, 3, OR 24 PHASES AVAILABLE
R4XXXX | 7D1 | 2001 | 7D2 | 2002 | 16-BIT INTEGER | R | DEMAND_WINDOW_OFFSET | DEMAND WINDOW |  | 5, 15, OR 30 MINUTES AVAILABLE
R4XXXX | 7D2 | 2002 | 7D3 | 2003 | 16-BIT INTEGER | R | I_MULTIPLIER_TYPE_OF | CURRENT MULTIPLIER |  | INTERNAL CALIBRATION VALUE
R4XXXX | 7D3 | 2003 | 7D4 | 2004 | 16-BIT INTEGER | R | NUM_PULSE_CTRS_OFFSE | NUMBER OF PULSE COUNTERS |  | NUMBER OF EXTERNAL PULSE INPUTS INSTALLED
R4XXXX | 7D4 | 2004 | 7D5 | 2005 | 16-BIT INTEGER | R | OVERLAP_OFFSET | DEMAND WINDOW OVERLAP |  | NUMBER OF ADJACENT DEMAND WINDOWS THAT ARE AVERAGED TO DETERMINE PEAK DEMAND
R4XXXX | 7D5 | 2005 | 7D6 | 2006 | 16-BIT INTEGER | R | NUM_TOUS_OFFSET | NUMBER OF TOU's |  | NUMBER OF DIFFERENT TOU PERIODS DEFINED IN THE TIME-OF-USE TABLE

## Notes
For a 32 bit integer, the first register contains the msb (top 16 bits of the 32 bits), and the second register the lower 16 bits of 32 bits.
For a 32 bit float, it is transmitted as a 32 bit integer (two registers, top 16 bits first). You need separate routines to convert 32 bit integers to IEEE (ANSI) floating point values. In a nutshell:
The msb (bit 31) of a 32 bit float is the sign bit, 0 is positive
The bits 23-30 are the exponent. Convert it to an integer and subtract the bias, then raise to to that power. The bias is 128
The low bits (0-22) are the mantissa. Divide them by 2^23, add 1.0 and multiply by the sign and the exponent to get the float